## Cover Page
Instructions Sheet (MSW1: Small Domestic/ Combined Water Service Connection*) *2-inch and smaller diameter water service connection is classified as small service connection and 3-inch and larger diameter water service connection is classified as large service connection
DIM*- Domestic Irrigation Mechanical (sum of all)
WSFU*= Water Supply Fixture Units
Page 1:
Step 1: Enter the project address, square #, lot #, DC Water Tracking #, and DCRA Tracking # as applicable at the top of the page. This information will populate top of all other sheets.
Step 2: Select the type of predominant supply systems (flush tanks or flushometer valves).
Step 3: Enter the total number of fixtures for each fixture type, as applicable. The total number of fixtures should include all the existing fixtures to remain and all the proposed fixtures to be added, as applicable. The spreadsheet will calculate the total WSFU and the resultant domestic demand in GPM.
Page 2:
Step 4: Select the type of building structure (One- or Two-Family Structure or Other Structure).
Step 5: Select the proposed meter type (domestic service only or combined fire and domestic service).
Step 6: Enter the total hose bibs and/ or lawn sprinkler, total continuous mechanical, and total intermittent mechanical demands, as applicable. Total DIM* demand is calculated by adding domestic, irrigation, and mechanical demands.
Step 7: Select whether or not a booster pump is proposed.
Step 8: If a booster pump is proposed, enter the pumped demand. The maximum DIM* demand is calculated based on the Total DIM* and pumped demand.
Step 9: Enter the fire flow demand, if there is a fire supression system.
Step 10: Indicate whether or not a fire pump is proposed. If a fire pump is proposed, enter the pumped fire demand.
Step 11: Compute maximum DIM* demand in WSFU.
Step 12: Go to Page 3 to compute the maximum developed lengths.
Step 13: Go to Page 3 to compute the minimum available pressures.
Step 14: Use pipe sizing chart on Pages 4 & 5 to select the domestic service pipe and distribution pipe sizes based on the WSFU, maximum developed length, and minimum available pressure for the domestic service.
Step 15: Determine the domestic/ SAF meter size based on AWWA water meter table on Page 3.
Step 16: If the service is combined, determine the fire service and distribution pipes sizes per construction code requirements or by hydraulic calculations in accordance with NFPA 13D, NFPA 13R, or NFPA 13, as applicable.
Step 17: If this is a combined service, enter the maximum combined demand in WSFU.
Step 18: Use pipe sizing charts on pages 4 & 5 to select the service pipe size based on the WSFU, maximum developed length, and minimum available pressure for the combined service.
Step 19: Determine the combined meter size based on AWWA water meter table on Page 3.

## Page 1
Project Address: |  |  |  |  | Water Supply Fixture Units Worksheet (MSW1)
Square #:
Lot #:
DC Water Tracking #:
DCRA Tracking #:
Input Cells
Predominant Supply Systems:
|  |  | Fixture Type | Occupancy | Type of Supply Control |  | Number of Fixtures |  |  | Load Value |  | WSFU
|  |  | Full-bath group** | Private | Flush Tank |  |  |  | x | 3.6 | =
|  |  |  | Private | Flushometer Valve |  |  |  | x | 8 | =
|  |  | Half-bath Group** | Private | Flush Tank |  |  |  | X | 2.6 | =
|  |  | Bathtub (with/ without shower head) | Private | Faucet |  |  |  | x | 1.4 | =
|  |  |  | Public | Faucet |  |  |  | x | 4 | =
|  |  | Bidet | Private | Faucet |  |  |  | x | 2 | =
|  |  | Combination fixture | Private | Faucet |  |  |  | x | 3 | =
|  |  | Dishwashing machine | Private | Automatic |  |  |  | x | 1.4 | =
|  |  | Drinking Fountain | Office, etc. | 3/8" Valve |  |  |  | x | 0.25 | =
|  |  | Kitchen sink | Private | Faucet |  |  |  | x | 1.4 | =
|  |  |  | Commercial | Faucet |  |  |  | x | 3 | =
|  |  | Laundry tub** | Private | Faucet |  |  |  | x | 1.4 | =
|  |  | Lavatory sink | Private | Faucet |  |  |  | x | 0.7 | =
|  |  |  | Public | Faucet |  |  |  | x | 2 | =
|  |  | Service sink | Public | Faucet |  |  |  | x | 3 | =
|  |  | Shower head | Private | Mixing Valve |  |  |  | x | 1.4 | =
|  |  |  | Public | Mixing Valve |  |  |  | x | 3 | =
|  |  | Urinal** | Public | 1" Flushometer Valve |  |  |  | x | 10 | =
|  |  |  | Public | 3/4" Flushometer Valve |  |  |  | x | 5 | =
|  |  |  | Public | Flush Tank |  |  |  | x | 3 | =
|  |  | Washing machine (8 lb) | Private | Automatic |  |  |  | x | 1.4 | =
|  |  | Washing machine (8 lb) | Public | Automatic |  |  |  | X | 3 | =
|  |  | Washing machine (15 lb) | Public | Automatic |  |  |  | x | 4 | =
|  |  | Water closet** | Private | Flush Tank |  |  |  | x | 2.2 | =
|  |  |  | Private | Flushometer Valve |  |  |  | x | 6 | =
|  |  |  | Private | Flushometer Tank |  |  |  | x | 2 | =
|  |  |  | Public | Flushometer Valve |  |  |  | x | 10 | =
|  |  |  | Public | Flush Tank |  |  |  | x | 5 | =
|  |  |  | Public | Flushometer Tank |  |  |  | x | 2 | =
|  |  | Other | [5 empty] | x | 5 | =
Total WSFU:
| 1 Domestic demand is calculated as per International Plumbing Code 2012 edition. | [6 empty] | Domestic Demand 1: | [5 empty] | GPM
** See the definition on page 6
DC Water Use Only
Reviewer's Name: | [5 empty] | Date: |  |  |  |  | The application is:
Approved
Comment: | [10 empty] | Not Approved
Flush Tank
Flushometer Valve

## Page 2
Project Address: |  |  | 0 |  | Meter Sizing Worksheet (MSW1)
Square #: |  |  | 0
Lot #: |  |  | 0
DC Water Tracking #: |  |  | 0
DCRA Tracking #: |  |  | 0
Input Cells
| Domestic Meter Size | [5 empty] | Fire Service
| a | Total Water Supply Fixture Units (WSFU) |  |  |  | wsfu | m | Total Fire Flow Demand (Per NFPA requirements) |  |  | gpm
| b | Domestic Demand |  |  |  | gpm
| c | Total Hose Bibs and/ or Lawn Sprinkler Demand |  |  |  | gpm | n | Fire Pump Proposed? |  |  | Yes/ No
| d | Total Continuous Mechanical Demand |  |  |  | gpm | o | Pumped Demand |  |  | gpm
| e | Total Intermittent Mechanical Demand |  |  |  | gpm | p | Maximum Fire Demand |  |  | gpm
| f | Total DIM (Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.)) Demand |  |  |  | gpm | q | Maximum Fire Demand in WSFU |  |  | wsfu
[7 empty] | Fire Service Pipe Size3 |  |  |  | in
| g | Domestic Booster Pump Proposed? |  |  |  |  | Fire Distribution Pipe Size3 |  |  |  | in
| h | Pumped Demand |  |  |  | gpm
| i | Maximum DIM Demand (higher of g and h) |  |  | 0 | gpm | Below Section is only Applicable to Meter for Combined Domestic and Fire Services
| j | Maximum DIM Demand in WSFU |  |  |  | wsfu
[7 empty] | r | Total Combined Demand |  |  | gpm
| k | The Maximum Developed Length Sheet A |  |  |  | ft
| l | Minimum Available Pressure Sheet A |  |  |  | psi | s | Total Combined Demand in WSFU4 |  |  | wsfu
| Domestic Service Pipe1 Size |  |  |  |  | in
[7 empty] | t | The Maximum Developed Length (Combined Service) |  |  | ft
| Domestic Distribution Pipe2 Size |  |  |  |  | in
[7 empty] | u | Minimum Available Pressure (Combined Service) |  |  | psi
| SAF Meter Size** |  |  |  |  | in
[7 empty] | Combined Service5 Pipe Size |  |  |  | in
DIM- Domestic Irrigation Mechanical
| SAF- System Availability Fee | [5 empty] | Combined Meter Size6 |  |  |  | in
Note: If the developed length or water supply fixture units value falls outside the pipe sizing chart, this spreadsheet can not be used for the pipe sizing. The designer can provide either pipe sizing computations per IPC or he/she can use the modified version of the meter sizing worksheet.
**Domestic meter size shall be computed based on the maximum DIM demand excluding fire demand. See AWWA water meter standards on Page 3 to determine domestic meter size. SAF meter size will be same as domestic meter size. The System Availability Fee (SAF) will be based on SAF meter size.
**SAF meter size shall be computed based on the maximum DIM demand excluding fire demand. See AWWA water meter standards on Page 3 to determine SAF meter size based on the maximum DIM demand. The System Availability Fee (SAF) will be based on SAF meter size.
Designer’s Name: |  |  |  | Designer’s Signature: |  |  |  |  | DC License #
Combined Fire and Domestic Service
Domestic Service Only
Proposed Meter Type:
Yes
No
One- or Two-Family Structure
Other Structure
1Service Pipe- The pipe from the water main to the water distribution system of the building served. The minimum service pipe size shall be 1" for new construction.
2Distribution Pipe- A pipe within the building structure from the water service pipe to the points of utilization.
3The fire service and distribution pipes shall be sized per construction code requirements or by hydraulic calculation in accordance with NFPA 13D, NFPA 13R, or NFPA 13, as applicable. The minimum service pipe size shall be 1" for new construction.
4If the designed value of the combined demand in WSFU is different from the above computed value, provide alternative computations per IPC/ IFC for the combined service line pipe size.
5The combined service shall be capable of supplying the simultaneous domestic demand and the sprinkler demand required to be hydraulically calculated by NFPA 13, NFPA 13D or NFPA 13R.
6See AWWA water meter standards on Page 3 to determine the proposed combined service meter size.

## Page 3
Project Address: |  |  | 0 | Sheet A (MSW1)
Square #: |  |  | 0
Lot #: |  |  | 0
DC Water Tracking #: |  |  | 0
DCRA Tracking #: |  |  | 0
Input Cells
| Maximum Developed Length | [5 empty] | AWWA Water Meter Standards
| The maximum developed length= (Actual length of pipe between the source of supply and the most remote fixture) X 1.2. | [5 empty] | Meter Size | High-Normal Flow Rate, gpm | Maximum Flow Rate, gpm
[5 empty] | Dom./ Fire5 |  | 5/8" EX. ONLY (PD*) | 10 | 20
| a | Distance from water main to curb1 |  |  |  | ft | 3/4" EX. ONLY (PD*) | 15 | 30
| b | Distance from curb to building face |  |  |  | ft | 1" (PD*) | 25 | 50
| c | Building Length (at the longest point) |  |  |  | ft | 1-1/2" (PD*) | 50 | 100
| d | Building Width (at the widest point) |  |  |  | ft | 2" (PD*) | 80 | 160
| e | Building Height2 |  |  |  | ft | Source: AWWA, M22, 3rd Ed.
| f | Length of pipe between source of supply and the most remote fixture (a+b+c+d+e or user entered value)3 |  |  |  | ft | PD*- Positive Displacement
| g | The maximum developed length (value f x 1.2) |  |  |  | ft
Minimum Available Pressure
Minimum available pressure = minimum static pressure available from the supply source - static pressure loss due to difference in elevations between the water supply source and the highest water supply outlet - meter loss - backflow prevention device/ assembly loss- any other loss (if any).
Dom./ Fire5
| h | Minimum static pressure available from the supply source4 |  |  |  | psi
| i | Static pressure loss (building height/2.31) |  | - | 0 | psi
| j | Additional static pressure loss (if any) |  | - |  | psi
| k | Meter loss6 |  | - |  | psi
| l | Backflow prevention device/ assembly loss6 |  | - |  | psi
| m | Any other loss |  | - |  | psi
| n | Pressure gain due to pump (if any) |  | + |  | psi
| o | Minimum available pressure (g-h-i-j-k-l+m) |  | = |  | psi
1This number can be obtained from DC Water by filling out 'Request For Information Form (Meter Sizing Worksheet)'. The form is available on DC Water's website. This number will be negative if the water main is between the road curb and the property line.
2Distance from ground to ceiling of the highest story.
3This value can be overridden if the actual length of the pipe is based on the design data.
4This number can be obtained from DC Water by filling out 'Request For Information Form (Meter Sizing Worksheet)'. The form is available on DC Water's website.
5Provide this information either for domestic service pipe or fire service pipe whichever is hydrulically more remote.
6See pressure loss values based on AWWA standards on Pages 7, 8, and 9 of this worksheet for a reference.

## Conversion Sheet A (hidden)
System Type | FlushTank |  |  | FlushTank |  | FlushometerValve
|  |  |  | WSFU | GPM | WSFU | GPM | Domestic Demand WFSU to GPM (FlushTank)
| WSFU | Demand |  | 1 | 3 | 1 | 15 | Row | #N/A | Row | #N/A
Domestic Demand |  | #N/A |  | 2 | 5 | 2 | 15 | GPM | #N/A | GPM | #N/A
| #N/A | 0 |  | 3 | 6.5 | 3 | 15 | WSFUs | #N/A | WSFUs | #N/A
Fire Demand | #N/A |  | #N/A | 4 | 8 | 4 | 15
|  |  |  | 5 | 9.4 | 5 | 15 | Slope | 0
Combined Demand |  |  |  | 6 | 10.7 | 6 | 17.4 | GPM | #N/A
System Type | FlushTank |  |  | 7 | 11.8 | 7 | 19.8
| WSFU | Demand |  | 8 | 12.8 | 8 | 22.2 | Domestic GPM to WSFU (FlushTank) |  |  |  | Fire GPM to WSFU (FlushTank or Flushometer Valve)
| #N/A |  |  | 9 | 13.7 | 9 | 24.6 | Row | #N/A | Row | #N/A | Row | #N/A | Row | #N/A
System Type | Flushometer Valve |  |  | 10 | 14.6 | 10 | 27 | WSFUs | #N/A | WSFUs | #N/A | WSFUs | #N/A | WSFUs | #N/A
| WSFU | Demand |  | 11 | 15.4 | 11 | 27.8 | GPM | #N/A | GPM | #N/A | GPM | #N/A | GPM | #N/A
| #N/A | 0 |  | 12 | 16 | 12 | 28.6
|  |  |  | 13 | 16.5 | 13 | 29.4 | Slope | 0 |  |  | Slope | 0
System Type | Flushometer Valve |  |  | 14 | 17 | 14 | 30.2 | WSFU | #N/A |  |  | WSFU | #N/A
| WSFU | Demand |  | 15 | 17.5 | 15 | 31
Domestic Demand |  | #N/A |  | 16 | 18 | 16 | 31.8
| #N/A | 0 |  | 17 | 18.4 | 17 | 32.6
Fire Demand | #N/A |  |  | 18 | 18.8 | 18 | 33.4 | Domestic Demand WFSU to GPM (FlushometerValve)
|  |  |  | 19 | 19.2 | 19 | 34.2 | Row | #N/A | Row | #N/A
|  |  |  | 20 | 19.6 | 20 | 35 | GPM | #N/A | GPM | #N/A
FlushTank/ Flushometer Valve Value | 1 |  |  | 25 | 21.5 | 25 | 38 | WSFUs | #N/A | WSFUs | #N/A
|  |  |  | 30 | 23.3 | 30 | 42
|  |  |  | 35 | 24.9 | 35 | 44 | Slope | 0
Booster Pump Value | 1 | IF(OR(s16=" ", 0)," ",s16) |  | 40 | 26.3 | 40 | 46 | GPM | #N/A
|  |  |  | 45 | 27.7 | 45 | 48
Fire Pump Value |  |  |  | 50 | 29.1 | 50 | 50 | Domestic GPM to WSFU (FlushometerValve)
|  |  |  | 60 | 32 | 60 | 54 | Row | #N/A | Row | #N/A
Type of Occupancy value | 2 |  |  | 70 | 35 | 70 | 58 | WSFUs | #N/A | WSFUs | #N/A
|  |  |  | 80 | 38 | 80 | 61.2 | GPM | #N/A | GPM | #N/A
Proposed Meter Type Value | 1 |  |  | 90 | 41 | 90 | 64.3
|  |  |  | 100 | 43.5 | 100 | 67.5 | Slope | 0
|  |  |  | 120 | 48 | 120 | 73 | WSFU | #N/A
Proposed Fire Pump | Input | Output |  | 140 | 52.5 | 140 | 77
| Yes | 1 |  | 160 | 57 | 160 | 81
| No |  |  | 180 | 61 | 180 | 85.5 | Combined GPM to WSFU (FlushTank)
|  |  |  | 200 | 65 | 200 | 90 | Row | #N/A | Row | #N/A
|  |  |  | 225 | 70 | 225 | 95.5 | WSFUs | #N/A | WSFUs | #N/A
|  |  |  | 250 | 75 | 250 | 101 | GPM | #N/A | GPM | #N/A
|  |  |  | 275 | 80 | 275 | 104.5
|  |  |  | 300 | 85 | 300 | 108 | Slope | 0
|  |  |  | 400 | 105 | 400 | 127 | WSFU | #N/A
|  |  |  | 500 | 124 | 500 | 143
|  |  |  | 750 | 170 | 750 | 177
|  |  |  | 1000 | 208 | 1000 | 208 | Combined GPM to WSFU (FlushometerValve)
|  |  |  | 1250 | 239 | 1250 | 239 | Row | #N/A | Row | #N/A
|  |  |  | 1500 | 269 | 1500 | 269 | WSFUs | #N/A | WSFUs | #N/A
|  |  |  | 1750 | 297 | 1750 | 297 | GPM | #N/A | GPM | #N/A
|  |  |  | 2000 | 325 | 2000 | 325
|  |  |  | 2500 | 380 | 2500 | 380 | Slope | 0
|  |  |  | 3000 | 433 | 3000 | 433 | WSFU | #N/A
|  |  |  | 4000 | 525 | 4000 | 525
|  |  |  | 5000 | 593 | 5000 | 593

## PSC 30-39 and 40-49
PIPE SIZING CHART (PRESSURE RANGE 30-39 PSI AND 40-49 PSI)
PIPE SIZING CHART FOR PRESSURE RANGE 30-39 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 2.5 | 2 | 1.5 | 1.5 | 1 | 1 | 0.5 | 0.5 | 0 | 0 | 0.75 | 0.5
| 9.5 | 7.5 | 6 | 5.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.5 | 0.75 | 0.75
| 32 | 25 | 20 | 16.5 | 11 | 9 | 7.8 | 6.5 | 5.5 | 4.5 | 0.75 | 1
| 32 | 32 | 27 | 21 | 13.5 | 10 | 8 | 7 | 5.5 | 5 | 1 | 1
| 32 | 32 | 32 | 32 | 30 | 24 | 20 | 17 | 13 | 10.5 | 0.75 | 1.25
| 80 | 80 | 70 | 61 | 45 | 34 | 27 | 22 | 16 | 12 | 1 | 1.25
| 80 | 80 | 80 | 75 | 54 | 40 | 31 | 25 | 17.5 | 13 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 84 | 73 | 64 | 56 | 45 | 36 | 1 | 1.5
| 151 | 151 | 151 | 151 | 117 | 92 | 79 | 69 | 54 | 43 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 128 | 99 | 83 | 72 | 56 | 45 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 1 | 2
| 275 | 275 | 275 | 275 | 258 | 223 | 196 | 174 | 144 | 122 | 1.5 | 2
| 365 | 365 | 365 | 365 | 318 | 266 | 229 | 201 | 160 | 134 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 495 | 448 | 409 | 353 | 311 | 2 | 2.5
PIPE SIZING CHART FOR PRESSURE RANGE 40-49 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 3 | 2.5 | 2 | 1.5 | 1.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.75 | 0.5
| 9.5 | 9.5 | 8.5 | 7 | 5.5 | 4.5 | 3.5 | 3 | 2.5 | 2 | 0.75 | 0.75
| 32 | 32 | 32 | 26 | 18 | 13.5 | 10.5 | 9 | 7.5 | 6 | 0.75 | 1
| 32 | 32 | 32 | 32 | 21 | 15 | 11.5 | 9.5 | 7.5 | 6.5 | 1 | 1
| 32 | 32 | 32 | 32 | 32 | 32 | 32 | 27 | 21 | 16.5 | 0.75 | 1.25
| 80 | 80 | 80 | 80 | 65 | 52 | 42 | 35 | 26 | 20 | 1 | 1.25
| 80 | 80 | 80 | 80 | 75 | 59 | 48 | 39 | 28 | 21 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 78 | 65 | 55 | 1 | 1.5
| 151 | 151 | 151 | 151 | 151 | 130 | 109 | 93 | 75 | 63 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 151 | 139 | 115 | 98 | 77 | 64 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1 | 2
| 275 | 275 | 275 | 275 | 275 | 275 | 264 | 238 | 198 | 169 | 1.5 | 2
| 365 | 365 | 365 | 365 | 365 | 349 | 304 | 270 | 220 | 185 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 533 | 533 | 528 | 456 | 403 | 2 | 2.5
Source: International Plumbing Code 2012 edition

## PSC 50-59 and 60+
PIPE SIZING CHART (PRESSURE RANGE 50-59 PSI AND 60+ PSI)
PIPE SIZING CHART FOR PRESSURE RANGE 50-59 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 3 | 3 | 2.5 | 2 | 1.5 | 1 | 1 | 1 | 0.5 | 0.5 | 0.75 | 0.5
| 9.5 | 9.5 | 9.5 | 8.5 | 6.5 | 5 | 4.5 | 4 | 3 | 2.5 | 0.75 | 0.75
| 32 | 32 | 32 | 32 | 25 | 18.5 | 14.5 | 12 | 9.5 | 8 | 0.75 | 1
| 32 | 32 | 32 | 32 | 30 | 22 | 16.5 | 13 | 10 | 8 | 1 | 1
| 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 29 | 24 | 0.75 | 1.25
| 80 | 80 | 80 | 80 | 80 | 68 | 57 | 48 | 35 | 28 | 1 | 1.25
| 80 | 80 | 80 | 80 | 80 | 75 | 63 | 53 | 39 | 29 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 82 | 70 | 1 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 139 | 120 | 94 | 79 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 146 | 126 | 97 | 81 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1 | 2
| 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 247 | 213 | 1.5 | 2
| 365 | 365 | 365 | 365 | 365 | 365 | 365 | 329 | 272 | 232 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 486 | 2 | 2.5
PIPE SIZING CHART FOR PRESSURE RANGE OVER 60 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 3 | 3 | 3 | 2.5 | 2 | 1.5 | 1.5 | 1 | 1 | 0.5 | 0.75 | 0.5
| 9.5 | 9.5 | 9.5 | 9.5 | 7.5 | 6 | 5 | 4.5 | 3.5 | 3 | 0.75 | 0.75
| 32 | 32 | 32 | 32 | 32 | 24 | 19.5 | 15.5 | 11.5 | 9.5 | 0.75 | 1
| 32 | 32 | 32 | 32 | 32 | 28 | 28 | 17 | 12 | 9.5 | 1 | 1
| 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 0.75 | 1.25
| 80 | 80 | 80 | 80 | 80 | 80 | 69 | 60 | 46 | 36 | 1 | 1.25
| 80 | 80 | 80 | 80 | 80 | 80 | 76 | 65 | 50 | 38 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 84 | 1 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 151 | 144 | 114 | 94 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 118 | 97 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1 | 2
| 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 252 | 1.5 | 2
| 365 | 368 | 368 | 368 | 368 | 368 | 368 | 368 | 318 | 273 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 2 | 2.5
Source: International Plumbing Code 2012 edition

## Definitions
DEFINITIONS (MSW1)
Full-bath Group (Flush Tank) - 1 Tank Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Full-bath Group (Flushometer Valve)- 1 Flushometer Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Half-bath Group (Flush Tank)- 1 Tank Toilet and 1 Bathroom Sink
Bathtub / Shower Combination- This fixture has a bathtub as the basin base with a bath shower atop it and is located in PRIVATE space. This fixture can only use either the tub faucet OR the shower head. Not both at the same time.
Combination Fixture- This fixture combines the functions of a sink and a toilet into a single fixture and is located in PRIVATE space.
Water Closet (Tank Toilet)- This is a toilet that has a tank on the back that holds water. If there is no tank the fixture is called a Flushometer Valve toilet.
Water Closet (Flushometer Valve)- This type of toilet has no tank to store the water on the back. The water pipe comes directly out of the wall and fills the bowl.
Water Closet (Flushometer Tank)- This fixture combines a Flushometer Valve with a tank. The valve allows a certain amount of water to fill the tank quickly at a high rate.
Laundry Tub- A sink located in a laundry room or utility room.
Hose Bibs (ALL Public and Private Bibs)- An outside faucet.
Urinal (1" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 1" valve.
Urinal (3/4" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 3/4" valve.
Urinal (Flush Tank)- A bathroom urinal located in PUBLIC space with a tank.
Domestic Demand- The water used by the fixtures and the mechanical equipment excluding fire and irrigation only.
IPC- International Plumbing Code

## Meter Losses
Pressure Loss Through Water Meters, PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Meter Size, in.
|  | 0.625 | 0.75 | 1 | 1.5 | 2
| 1 | 0.04 | 0.01679 | 0.0060131
| 2 | 0.15111 | 0.067159 | 0.024053
| 3 | 0.34 | 0.15111 | 0.054118
| 4 | 0.60445 | 0.26863 | 0.09621
| 5 | 0.94445 | 0.41974 | 0.15033
| 6 | 1.36 | 0.60443 | 0.21647
| 7 | 1.8511 | 0.82269 | 0.29464
| 8 | 2.4178 | 1.0745 | 0.38484 | 0.095737
| 9 | 3.06 | 1.36 | 0.48706 | 0.12117
| 10 | 3.7778 | 1.679 | 0.60131 | 0.14959
| 11 | 4.5711 | 2.0315 | 0.72759 | 0.181
| 12 | 5.44 | 2.4177 | 0.86589 | 0.21541
| 13 | 6.3845 | 2.8375 | 1.0162 | 0.25281 | 0.099091
| 14 | 7.4045 | 3.2908 | 1.1786 | 0.29319 | 0.11492
| 15 | 8.5001 | 3.7777 | 1.353 | 0.33657 | 0.13193
| 16 | 9.6712 | 4.2982 | 1.5394 | 0.38295 | 0.1501
| 17 | 10.9179 | 4.8522 | 1.7378 | 0.43231 | 0.16945
| 18 | 12.2401 | 5.4399 | 1.9483 | 0.48467 | 0.18997
| 19 | 13.6379 | 6.0611 | 2.1707 | 0.54002 | 0.21167
| 20 | 15.1112 | 6.7159 | 2.4053 | 0.59836 | 0.23453
| 22 |  | 8.1262 | 2.9104 | 0.72401 | 0.28379
| 24 |  | 9.6708 | 3.4636 | 0.86163 | 0.33773
| 26 |  | 11.3498 | 4.0649 | 1.0112 | 0.39636
| 28 |  | 13.1631 | 4.7143 | 1.1728 | 0.45969
| 30 |  | 15.1107 | 5.4118 | 1.3463 | 0.5277
| 32 |  |  | 6.1574 | 1.5318 | 0.60041
| 34 |  |  | 6.9512 | 1.7292 | 0.67781
| 36 |  |  | 7.793 | 1.9387 | 0.75989
| 38 |  |  | 8.683 | 2.1601 | 0.84667
| 40 |  |  | 9.621 | 2.3934 | 0.93814
| 42 |  |  | 10.6072 | 2.6387 | 1.0343
| 44 |  |  | 11.6414 | 2.896 | 1.1351
| 46 |  |  | 12.7238 | 3.1653 | 1.2407
| 48 |  |  | 13.8543 | 3.4465 | 1.3509
| 50 |  |  | 15.0328 | 3.7397 | 1.4658
| 52 |  |  |  | 4.0449 | 1.5855
| 54 |  |  |  | 4.362 | 1.7098
| 56 |  |  |  | 4.6911 | 1.8388
| 58 |  |  |  | 5.0322 | 1.9724
| 60 |  |  |  | 5.3852 | 2.1108
| 65 |  |  |  | 6.3201 | 2.4773
| 70 |  |  |  | 7.3299 | 2.8731
| 75 |  |  |  | 8.4144 | 3.2981
| 80 |  |  |  | 9.5737 | 3.7526
| 85 |  |  |  | 10.8078 | 4.2363
| 90 |  |  |  | 12.1167 | 4.7493
| 95 |  |  |  | 13.5004 | 5.2917
| 100 |  |  |  | 14.9589 | 5.8634
| 110 |  |  |  |  | 7.0947
| 120 |  |  |  |  | 8.4433
| 130 |  |  |  |  | 9.9091
| 140 |  |  |  |  | 11.4922
| 150 |  |  |  |  | 13.1926
| 160 |  |  |  |  | 15.0102

## DCV Losses
Pressure Loss Through BPA* (DCV), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 0.75 | 1 | 1.5 | 2
| 1 | 4.0068 | 4.0024 | 4.0006 | 4.0002
| 2 | 4.0271 | 4.0095 | 4.0024 | 4.0009
| 3 | 4.0611 | 4.0214 | 4.0054 | 4.0021
| 4 | 4.1086 | 4.038 | 4.0096 | 4.0037
| 5 | 4.1697 | 4.0593 | 4.0151 | 4.0058
| 6 | 4.2443 | 4.0854 | 4.0217 | 4.0084
| 7 | 4.3326 | 4.1163 | 4.0295 | 4.0114
| 8 | 4.4344 | 4.1519 | 4.0386 | 4.0149
| 9 | 4.5498 | 4.1923 | 4.0488 | 4.0189
| 10 | 4.6787 | 4.2374 | 4.0603 | 4.0233
| 11 | 4.8213 | 4.2872 | 4.0729 | 4.0282
| 12 | 4.9774 | 4.3418 | 4.0868 | 4.0336
| 13 | 5.1471 | 4.4011 | 4.1019 | 4.0394
| 14 | 5.3303 | 4.4652 | 4.1182 | 4.0457
| 15 | 5.5271 | 4.5341 | 4.1356 | 4.0525
| 16 | 5.7376 | 4.6076 | 4.1543 | 4.0597
| 17 | 5.9615 | 4.686 | 4.1742 | 4.0674
| 18 | 6.1991 | 4.769 | 4.1953 | 4.0755
| 19 | 6.4502 | 4.8569 | 4.2176 | 4.0842
| 20 | 6.7149 | 4.9494 | 4.2411 | 4.0932
| 22 | 7.2851 | 5.1488 | 4.2918 | 4.1128
| 24 | 7.9095 | 5.3672 | 4.3472 | 4.1343
| 26 | 8.5882 | 5.6046 | 4.4075 | 4.1576
| 28 | 9.3213 | 5.8609 | 4.4726 | 4.1828
| 30 | 10.1086 | 6.1362 | 4.5425 | 4.2098
| 32 |  | 6.4306 | 4.6173 | 4.2387
| 34 |  | 6.7439 | 4.6969 | 4.2695
| 36 |  | 7.0762 | 4.7813 | 4.3021
| 38 |  | 7.4275 | 4.8705 | 4.3366
| 40 |  | 7.7978 | 4.9645 | 4.373
| 42 |  | 8.187 | 5.0634 | 4.4112
| 44 |  | 8.5953 | 5.1671 | 4.4513
| 46 |  | 9.0225 | 5.2756 | 4.4933
| 48 |  | 9.4688 | 5.3889 | 4.5371
| 50 |  | 9.934 | 5.5071 | 4.5828
| 52 |  |  | 5.63 | 4.6304
| 54 |  |  | 5.7578 | 4.6798
| 56 |  |  | 5.8904 | 4.7311
| 58 |  |  | 6.0279 | 4.7842
| 60 |  |  | 6.1702 | 4.8392
| 65 |  |  | 6.5469 | 4.9849
| 70 |  |  | 6.9538 | 5.1423
| 75 |  |  | 7.3909 | 5.3113
| 80 |  |  | 7.8581 | 5.492
| 85 |  |  | 8.3554 | 5.6843
| 90 |  |  | 8.8828 | 5.8883
| 95 |  |  | 9.4405 | 6.1039
| 100 |  |  | 10.0282 | 6.3312
| 110 |  |  |  | 6.8208
| 120 |  |  |  | 7.357
| 130 |  |  |  | 7.9398
| 140 |  |  |  | 8.5692
| 150 |  |  |  | 9.2452
| 160 |  |  |  | 9.9679
*BPA- Backflow Prevention Assemblies

## RPZ Losses
Pressure Loss Through BPA* (RPZ), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 0.75 | 1 | 1.5 | 2
| 1 | 10.0111 | 10.0032 | 10.0006 | 10.0002
| 2 | 10.0443 | 10.0127 | 10.0024 | 10.0009
| 3 | 10.0997 | 10.0285 | 10.0054 | 10.0021
| 4 | 10.1772 | 10.0506 | 10.0096 | 10.0037
| 5 | 10.2769 | 10.0791 | 10.0151 | 10.0058
| 6 | 10.3987 | 10.1139 | 10.0217 | 10.0084
| 7 | 10.5426 | 10.1551 | 10.0295 | 10.0114
| 8 | 10.7087 | 10.2025 | 10.0386 | 10.0149
| 9 | 10.897 | 10.2563 | 10.0488 | 10.0189
| 10 | 11.1074 | 10.3165 | 10.0603 | 10.0233
| 11 | 11.34 | 10.3829 | 10.0729 | 10.0282
| 12 | 11.5947 | 10.4557 | 10.0868 | 10.0336
| 13 | 11.8715 | 10.5349 | 10.1019 | 10.0394
| 14 | 12.1705 | 10.6203 | 10.1182 | 10.0457
| 15 | 12.4917 | 10.7121 | 10.1356 | 10.0525
| 16 | 12.835 | 10.8102 | 10.1543 | 10.0597
| 17 | 13.2004 | 10.9146 | 10.1742 | 10.0674
| 18 | 13.588 | 11.0254 | 10.1953 | 10.0755
| 19 | 13.9977 | 11.1425 | 10.2176 | 10.0842
| 20 | 14.4296 | 11.2659 | 10.2411 | 10.0932
| 22 | 15.3598 | 11.5318 | 10.2918 | 10.1128
| 24 | 16.3786 | 11.8229 | 10.3472 | 10.1343
| 26 | 17.486 | 12.1394 | 10.4075 | 10.1576
| 28 | 18.682 | 12.4812 | 10.4726 | 10.1828
| 30 | 19.9666 | 12.8483 | 10.5425 | 10.2098
| 32 |  | 13.2408 | 10.6173 | 10.2387
| 34 |  | 13.6585 | 10.6969 | 10.2695
| 36 |  | 14.1016 | 10.7813 | 10.3021
| 38 |  | 14.57 | 10.8705 | 10.3366
| 40 |  | 15.0637 | 10.9645 | 10.373
| 42 |  | 15.5827 | 11.0634 | 10.4112
| 44 |  | 16.1271 | 11.1671 | 10.4513
| 46 |  | 16.6967 | 11.2756 | 10.4933
| 48 |  | 17.2917 | 11.3889 | 10.5371
| 50 |  | 17.912 | 11.5071 | 10.5828
| 52 |  |  | 11.63 | 10.6304
| 54 |  |  | 11.7578 | 10.6798
| 56 |  |  | 11.8904 | 10.7311
| 58 |  |  | 12.0279 | 10.7842
| 60 |  |  | 12.1702 | 10.8392
| 65 |  |  | 12.5469 | 10.9849
| 70 |  |  | 12.9538 | 11.1423
| 75 |  |  | 13.3909 | 11.3113
| 80 |  |  | 13.8581 | 11.492
| 85 |  |  | 14.3554 | 11.6843
| 90 |  |  | 14.8828 | 11.8883
| 95 |  |  | 15.4405 | 12.1039
| 100 |  |  | 16.0282 | 12.3312
| 110 |  |  |  | 12.8208
| 120 |  |  |  | 13.357
| 130 |  |  |  | 13.9398
| 140 |  |  |  | 14.5692
| 150 |  |  |  | 15.2452
| 160 |  |  |  | 15.9679
*BPA- Backflow Prevention Assemblies