## Cover
Instructions Sheet (MSW3: Large Domestic and Large Fire Service Connections) *2-inch and smaller diameter water service connection is classified as small service connection and 3-inch and larger diameter water service connection is classified as large service connection
DIM*- Domestic Irrigation Mechanical
WSFU*= Water Supply Fixture Units
Instructions:
Page 1:
Step 1: Enter the project address, square #, lot #, DC Water Tracking #, and DOB Tracking # as applicable.
Step 2: Select the type of predominant supply systems (flush tanks or flushometer valves).
Step 3: Select the type of building occupancy (residential building or non-residential building).
Step 4: Enter the total number of fixtures for each fixture type as applicable. The total number of fixtures should include all the existing fixtures to remain and proposed fixtures to be added if the project is part of the building addition/ renovation/ alteration. The domestic demand is computed based on the total WSFU* and type of predominate supply systems.
Page 2:
Step 5: Select the proposed meter type (Separate Domestic and Fire Services or Combined Domestic and Fire Services).
Step 6: Enter the total hose bibs and/ or lawn sprinkler, total continuous mechanical, and total intermittent mechanical demands, as applicable. Total DIM* demand is calculated by adding domestic, irrigation, and mechanical demands.
Step 7: Select whether or not a booster pump is proposed.
Step 8: If the booster pump is proposed, enter the pump design and pump maximum demands. The maximum DIM* demand is calculated based on the DIM* and pump demands.
Step 9: Follow Table C: AWWA Water Meter Standards on Pg. 4 to select meter size based on the permissible flow rates.
Step 10: If a separate fire service is proposed, enter the total fire demand.
Step 11: Select whether or not a fire pump is proposed. If the fire pump is proposed, enter the fire pump flow rating.
Step 12: If the proposed service connection is combined (fire + domestic), the maximum combined demand is computed based on maximum DIM* and fire demand values.
Step 13: If the combined meter is proposed, follow Table C: AWWA Water Meter Standards on Pg. 3 to select combined meter size based on the permissible flow rates.
Page 3:
Step 14: Enter the pipe length between the supply main and the building, the proposed pipe size, C value, and other pipe losses for the domestic and fire service connections (as applicable) to calculate total pipe losses between the supply main and the building.
Step 15: Enter the supply main and highest fixture elevation to compute static head loss.
Step 16: Enter the hydrant flow test results.
Step 17: Enter the design pressure at the supply main.
Step 18: Enter the pressure losses due to meter, backflow prevention assembly, and special fixture, as applicable. Enter the pipe losses inside the building. Enter the pressure gain (if any) due to pumps.

## Page 1
|  |  | Water Supply Fixture Units Worksheet (MSW3) |  |  |  | Project Address:
Square #:
Lot #:
DC Water Tracking #:
DOB Tracking #:
Input Cells
| Predominant Supply Systems: |  |  |  |  | Type of Occupancy:
|  | Fixture Type |  | Occupancy | Type of Supply Control | Number of Fixtures |  |  | Load Value |  | WSFU
|  | Full-bath group** |  | Private | Flush Tank |  |  | x | 3.6 | =
|  |  |  | Private | Flushometer Valve |  |  | x | 8 | =
|  | Bathtub |  | Private | Faucet |  |  | x | 1.4 | =
|  |  |  | Public | Faucet |  |  | x | 4 | =
|  | Bidet |  | Private | Faucet |  |  | x | 2 | =
|  | Combination fixture |  | Private | Faucet |  |  | x | 3 | =
|  | Dishwashing machine |  | Private | Automatic |  |  | x | 1.4 | =
|  | Drinking Fountain |  | Office, etc. | 3/8" Valve |  |  | x | 0.25 | =
|  | Kitchen sink |  | Private | Faucet |  |  | x | 1.4 | =
|  |  |  | Commercial | Faucet |  |  | x | 3 | =
|  | Laundry trays (1-3) |  | Private | Faucet |  |  | x | 1.4 | =
|  | Lavatory sink |  | Private | Faucet |  |  | x | 0.7 | =
|  |  |  | Public | Faucet |  |  | x | 2 | =
|  | Service sink |  | Public | Faucet |  |  | x | 3 | =
|  | Shower head |  | Private | Mixing Valve |  |  | x | 1.4 | =
|  |  |  | Public | Mixing Valve |  |  | x | 3 | =
|  | Urinal** |  | Public | 1" Flushometer Valve |  |  | x | 10 | =
|  |  |  | Public | 3/4" Flushometer Valve |  |  | x | 5 | =
|  |  |  | Public | Flush Tank |  |  | x | 3 | =
|  | Washing machine (8 lb) |  | Private | Automatic |  |  | x | 1.4 | =
|  | Washing machine (8 lb) |  | Public | Automatic |  |  | X | 3 | =
|  | Washing machine (15 lb) |  | Public | Automatic |  |  | x | 4 | =
|  | Water closet** |  | Private | Flush Tank |  |  | x | 2.2 | =
|  |  |  | Private | Flushometer Valve |  |  | x | 6 | =
|  |  |  | Private | Flushometer Tank |  |  | x | 2 | =
|  |  |  | Public | Flushometer Valve |  |  | x | 10 | =
|  |  |  | Public | Flush Tank |  |  | x | 5 | =
|  |  |  | Public | Flushometer Tank |  |  | x | 2 | =
|  | Other | [5 empty] | x | 0 | =
|  | Other | [5 empty] | x | 0 | =
|  | Other | [5 empty] | x | 0 | =
Total WSFU2:
1Domestic demand is calculated as per International Plumbing Code 2012 edition. | [6 empty] | Domestic Demand1: | [5 empty] | GPM
2If the total WSFU is greater than 5000, this spreadsheet can not be used in calculating domestic demand. Provide an alternative method for computing the proposed domestic demand.
** See the definition on page 6

## Conversion Sheet A (hidden)
System Type | FlushTank |  | FlushTank |  | FlushometerValve
|  |  | WSFU | GPM | WSFU | GPM | Domestic Demand WFSU to GPM (FlushTank)
| WSFU | Demand | 1 | 3 | 1 | 15 | Row | #N/A | Row | #N/A
Domestic Demand |  | #N/A | 2 | 5 | 2 | 15 | GPM | #N/A | GPM | #N/A
|  |  | 3 | 6.5 | 3 | 15 | WSFUs | #N/A | WSFUs | #N/A
|  |  | 4 | 8 | 4 | 15
|  |  | 5 | 9.4 | 5 | 15 | Slope | 0
|  |  | 6 | 10.7 | 6 | 17.4 | GPM | #N/A
|  |  | 7 | 11.8 | 7 | 19.8
|  |  | 8 | 12.8 | 8 | 22.2
|  |  | 9 | 13.7 | 9 | 24.6
|  |  | 10 | 14.6 | 10 | 27
|  |  | 11 | 15.4 | 11 | 27.8
|  |  | 12 | 16 | 12 | 28.6
|  |  | 13 | 16.5 | 13 | 29.4
System Type | Flushometer Valve |  | 14 | 17 | 14 | 30.2
| WSFU | Demand | 15 | 17.5 | 15 | 31
Domestic Demand |  | #N/A | 16 | 18 | 16 | 31.8
|  |  | 17 | 18.4 | 17 | 32.6
|  |  | 18 | 18.8 | 18 | 33.4 | Domestic Demand WFSU to GPM (FlushometerValve)
|  |  | 19 | 19.2 | 19 | 34.2 | Row | #N/A | Row | #N/A
|  |  | 20 | 19.6 | 20 | 35 | GPM | #N/A | GPM | #N/A
|  |  | 25 | 21.5 | 25 | 38 | WSFUs | #N/A | WSFUs | #N/A
|  |  | 30 | 23.3 | 30 | 42
Supply Systems Predominantly |  |  | 35 | 24.9 | 35 | 44 | Slope | 0
Input Range |  |  | 40 | 26.3 | 40 | 46 | GPM | #N/A
Flush Tanks |  |  | 45 | 27.7 | 45 | 48
Flushometer Valves |  |  | 50 | 29.1 | 50 | 50
FlushTank/ Flushometer Valve Value | 1 |  | 60 | 32 | 60 | 54
|  |  | 70 | 35 | 70 | 58
Type of Occupancy: |  |  | 80 | 38 | 80 | 61.2
Residential Building |  |  | 90 | 41 | 90 | 64.3
Non-Residential Building |  |  | 100 | 43.5 | 100 | 67.5
2 |  |  | 120 | 48 | 120 | 73
|  |  | 140 | 52.5 | 140 | 77
|  |  | 160 | 57 | 160 | 81
|  |  | 180 | 61 | 180 | 85.5
|  |  | 200 | 65 | 200 | 90
|  |  | 225 | 70 | 225 | 95.5
|  |  | 250 | 75 | 250 | 101
|  |  | 275 | 80 | 275 | 104.5
|  |  | 300 | 85 | 300 | 108
|  |  | 400 | 105 | 400 | 127
|  |  | 500 | 124 | 500 | 143
|  |  | 750 | 170 | 750 | 177
|  |  | 1000 | 208 | 1000 | 208
|  |  | 1250 | 239 | 1250 | 239
|  |  | 1500 | 269 | 1500 | 269
|  |  | 1750 | 297 | 1750 | 297
|  |  | 2000 | 325 | 2000 | 325
|  |  | 2500 | 380 | 2500 | 380
|  |  | 3000 | 433 | 3000 | 433
|  |  | 4000 | 525 | 4000 | 525
|  |  | 5000 | 593 | 5000 | 593

## Page 2
|  |  |  | Meter Sizing Worksheet (MSW3) | [7 empty] | Project Address:
Square #:
Lot #:
DC Water Tracking #:
DOB Tracking #:
Input Cells
Proposed Meter Type:
| Domestic Meter Size | [8 empty] | Fire Demand
| a | Total Water Supply Fixture Units (WSFU) | [5 empty] | wsfu |  | l | Total Fire Demand (Per NFPA requirements) | [5 empty] | gpm
| b | Domestic Demand 1 | [5 empty] | gpm
| c | Total Hose Bibs and/ or Lawn Sprinkler Demand | [5 empty] | gpm |  | m | Fire Pump Proposed?
| d | Total Continuous Mechanical Demand | [5 empty] | gpm |  | n | Fire Pump Flow Rating | [5 empty] | gpm
| e | Total Intermittent Mechanical Demand | [5 empty] | gpm |  | Pump Test Demand (150% of Fire Pump Flow Rating) |  |  |  |  | 0 |  | gpm
| f | Total Continuous Demand (Hose Bibs and/ or Lawn Sprinkler + Continuous Mechanical) |  |  |  |  | 0 | gpm
[10 empty] | Maximum Fire Demand |  |  |  |  | 0 |  | gpm
| g | Total DIM (Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.)) Demand |  |  |  |  | 0 | gpm
| i | Domestic Booster Pump Proposed?
Below Section is only Applicable to Meter for Combined Domestic and Fire Services
| j | Pump Maximum Demand |  |  |  |  | 0 | gpm
| k | Maximum DIM* Demand |  |  |  |  | 0 | gpm |  | Maximum Combined Demand |  |  |  |  | NA |  | gpm
| Select System Availability Fee (SAF) Meter Size/ Domestic Meter Size 2 | [8 empty] | Select Combined Meter Size 3
| Is Maximum DIM* Demand is less than or equal to Allowable Maximum Flow Rate through Meter? | [5 empty] | NA |  |  | Is Maximum Combined Demand is less than or equal to Allowable Maximum Flow Rate through Meter? |  |  |  |  | NA
| Is Total Continuous Demand is less than or equal to Allowable High-Normal Flow Rate through Meter? | [5 empty] | NA
DIM*- Domestic Irrigation Mechanical
1 The domestic demand should be computed by using total Water Supply Fixture Units. The domestic demand value should be based on District of Columbia adopted current version of the International Plumbing Code (IPC) or International Residential Code (IRC) as applicable to the project. IPC or IRC has tables to determine demands based on type of supply systems (predominately used flush tanks or flushometers).
2 The System Availability Fee (SAF) meter size shall be computed for the peak water demand excluding fire demand. The domestic meter size will be same as SAF meter size for the separate domestic service meter. Use DC Water 'Table C- AWWA meter standards' to determine size of the meter
3 Combined meter size (domestic + fire) may be different from SAF meter size and will be determined based on combined flow demand. Use DC Water 'Table C- AWWA meter standards' to determine size of the meter.
By signing this document, the designer is responsible for determining required domestic, irrigation, mechanical, and fire flows in addition to the proper sizing of meters. By submitting this application, I affirm that the information provided is correct.
Designer’s Name: | [5 empty] | Designer’s Signature: | [7 empty] | DC License #:
Separate or Combined meter?
|  | Input Range | Separate Domestic and Fire Services
Combined Domestic and Fire Services
|  | Cell Link | 1
|  | SAF Meter |  | Domestic Pump? |  |  |  |  | Fire Pump?
|  | Input Range | NA | Input Range |  | YES |  |  | Input Range |  |  |  | YES
|  |  | 2" |  |  | NO | [6 empty] | NO
|  |  | 3" | Cell Link |  | 1 |  |  | Cell Link |  |  |  | 1
4"
6"
8"
|  | Cell Link | 1
|  | Allowable Maximum Flow Rate, gpm |  |  | #VALUE!
|  | Allowable High-Normal Flow Rate, gpm |  |  | #VALUE!
Combined Meter
|  | Input Range | NA
NA
NA
NA
NA
NA
|  | Cell Link | 1
|  | Allowable Maximum Flow Rate, gpm |  |  | #VALUE!
|  | Allowable High-Normal Flow Rate, gpm |  |  | #VALUE!

## Page 3
|  | Pipe Losses Computation Worksheet (MSW3) | [5 empty] | Project Address:
Square #:
Lot #:
DC Water Tracking #:
DOB Tracking #:
Input Cells
Table A- Total Pipe Losses (Main to the Bldg.) | [5 empty] | Hydrant Flow Test Results
Date of Test:
|  |  | Dom. | Fire | Comb. | Static Pressure, psi
a | Pipe Length (Main to Bldg.), ft |  |  |  |  | Residual Pressure, psi
b | Maximum Demand, gpm |  | 0 | 0 | NA
c | Pipe Size, inch |  |  |  |  | Available Pressure at the Highest Fixture
d | C Value | [9 empty] | Dom. |  | Fire |  | Comb.
e | Pipe Friction Losses, psi |  |  |  |  | l | Design Pressure at the Main, psi
f | Other Pipe Losses (if any), psi
g | Total Pipe Losses (Main to Bldg.), psi |  |  |  |  | m | Total Pipe Losses, psi (See Table A) |  |  | -
h | V (fps) 1 |  |  |  |  | n | Meter Loss2, psi |  |  | -
[6 empty] | o | Static Head Loss, psi (See Table B) |  |  | - | 0 |  | 0 |  | 0
[6 empty] | p | Backflow Prevention Assembly Loss, psi |  |  | -
[6 empty] | q | Pipe Losses inside the Building3, psi |  |  | -
Table B- Static Head Loss (Main to Highest Fixture) | [5 empty] | r | Special Fixture Loss- Other (if any), psi |  |  | -
|  |  | Dom. | Fire | Comb. | s | Pressure Gain due to the pump, psi |  |  | +
i | Supply Main Elevation, ft |  |  |  |  | t | Maximum Pressure Available at the Highest Fixture, psi |  |  | = | 0 |  | 0 |  | 0
j | Highest Fixture Elevation, ft
k | Static Head Loss, psi |  | 0 | 0 | 0
*Table C - AWWA Water Meter Standards
[6 empty] | Meter Size |  |  | High-Normal Flow Rate, gpm |  |  | Maximum Flow Rate, gpm
[6 empty] | 2" (PD) |  |  | 80 |  |  | 160
[6 empty] | 3" (Compound Class II) |  |  | 175 |  |  | 350
[6 empty] | 4" (Compound Class II) |  |  | 300 |  |  | 600
[6 empty] | 6" (Compound Class II) |  |  | 675 |  |  | 1350
[6 empty] | 8" (Compound Class II) |  |  | 900 |  |  | 1600
[6 empty] | 3" (FS) |  |  | 250 |  |  | 350
[6 empty] | 4" (FS) |  |  | 400 |  |  | 700
[6 empty] | 6" (FS) |  |  | 900 |  |  | 1600
[6 empty] | 8" (FS) |  |  | 1600 |  |  | 2800
[6 empty] | 10" (FS) |  |  | 2200 |  |  | 4400
Source: AWWA, M22, 3rd Ed.
PD - Positive Displacement
FS - Fire Service, type II-Compound
1The maximum recommended flow velocity is 15 fps for ductile iron pipe.
2Based on "AWWA Water Meter Standards" or meter manufactures' specifications.
3Values should be provided by the design engineer registered in District of Columbia.

## Page 4
| Domestic Demand vs Total WSFU* Chart |  | Project Address:
Square #:
Lot #:
DC Water Tracking#:
DOB Tracking #:
Total WSFUs: |  | Predominate Supply Systems: |  | Flush Tanks
Domestic Demand, gpm
WSFU*= Water Supply Fixture Units

## Page 5
DEFINITIONS (MSW1)
Full-bath Group (Flush Tank) - 1 Tank Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Full-bath Group (Flushometer Valve)- 1 Flushometer Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Half-bath Group (Flush Tank)- 1 Tank Toilet and 1 Bathroom Sink
Bathtub / Shower Combination- This fixture has a bathtub as the basin base with a bath shower atop it and is located in PRIVATE space. This fixture can only use either the tub faucet OR the shower head. Not both at the same time.
Combination Fixture- This fixture combines the functions of a sink and a toilet into a single fixture and is located in PRIVATE space.
Water Closet (Tank Toilet)- This is a toilet that has a tank on the back that holds water. If there is no tank the fixture is called a Flushometer Valve toilet.
Water Closet (Flushometer Valve)- This type of toilet has no tank to store the water on the back. The water pipe comes directly out of the wall and fills the bowl.
Water Closet (Flushometer Tank)- This fixture combines a Flushometer Valve with a tank. The valve allows a certain amount of water to fill the tank quickly at a high rate.
Laundry Tub- A sink located in a laundry room or utility room.
Hose Bibs (ALL Public and Private Bibs)- An outside faucet.
Urinal (1" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 1" valve.
Urinal (3/4" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 3/4" valve.
Urinal (Flush Tank)- A bathroom urinal located in PUBLIC space with a tank.
Domestic Demand- The water used by the fixtures and the mechanical equipment excluding fire and irrigation only.
IPC- International Plumbing Code

## Page 6
Pressure Loss Through Water Meters, PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Meter Size, in.
|  | 2 | 3 | 4 | 6
| 30 | 0.5277
| 32 | 0.60041
| 34 | 0.67781
| 36 | 0.75989
| 38 | 0.84667
| 40 | 0.93814
| 42 | 1.0343
| 44 | 1.1351
| 46 | 1.2407
| 48 | 1.3509
| 50 | 1.4658
| 52 | 1.5855
| 54 | 1.7098
| 56 | 1.8388
| 58 | 1.9724
| 60 | 2.1108
| 65 | 2.4773 | 0.51882
| 70 | 2.8731 | 0.6017
| 75 | 3.2981 | 0.69073
| 80 | 3.7526 | 0.7859
| 85 | 4.2363 | 0.88721
| 90 | 4.7493 | 0.99465
| 95 | 5.2917 | 1.1082
| 100 | 5.8634 | 1.228
| 110 | 7.0947 | 1.4858 | 0.45944
| 120 | 8.4433 | 1.7683 | 0.54678
| 130 | 9.9091 | 2.0753 | 0.6417
| 140 | 11.4922 | 2.4068 | 0.74422
| 150 | 13.1926 | 2.7629 | 0.85434
| 160 | 15.0102 | 3.1436 | 0.97205
| 170 |  | 3.5488 | 1.0974
| 180 |  | 3.9786 | 1.2302
| 190 |  | 4.433 | 1.3707
| 200 |  | 4.9119 | 1.5188
| 220 |  | 5.9434 | 1.8378
| 240 |  | 7.0731 | 2.1871 | 0.5124
| 260 |  | 8.3011 | 2.5668 | 0.60136
| 280 |  | 9.6273 | 2.9769 | 0.69743
| 300 |  | 11.0517 | 3.4174 | 0.80062
| 350 |  | 15.0426 | 4.6514 | 1.0897
| 400 |  |  | 6.0753 | 1.4233
| 450 |  |  | 7.6891 | 1.8014
| 500 |  |  | 9.4927 | 2.2239
| 600 |  |  | 13.6694 | 3.2025
| 650 |  |  | 16.0426 | 3.7585
| 700 |  |  |  | 4.3589
| 800 |  |  |  | 5.6933
| 900 |  |  |  | 7.2056
| 1000 |  |  |  | 8.8958
| 1100 |  |  |  | 10.7639
| 1200 |  |  |  | 12.8099
| 1300 |  |  |  | 15.0339

## Page 7
Pressure Loss Through BPA* (DCV), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 3 | 4 | 6 | 8
50
52
| 54 | 4.1709
| 56 | 4.1838 | 4.0748
| 58 | 4.1972 | 4.0802
| 60 | 4.211 | 4.0858
| 65 | 4.2476 | 4.1007
| 70 | 4.2872 | 4.1168 | 4.0295
| 75 | 4.3297 | 4.1341 | 4.0338
| 80 | 4.3751 | 4.1526 | 4.0385
| 85 | 4.4234 | 4.1723 | 4.0435
| 90 | 4.4747 | 4.1931 | 4.0487
| 95 | 4.5289 | 4.2152 | 4.0543 | 4.0212
| 100 | 4.5861 | 4.2384 | 4.0602 | 4.0235
| 110 | 4.7092 | 4.2885 | 4.0728 | 4.0284
| 120 | 4.8439 | 4.3433 | 4.0867 | 4.0338
| 130 | 4.9905 | 4.4029 | 4.1017 | 4.0396
| 140 | 5.1487 | 4.4673 | 4.1179 | 4.046
| 150 | 5.3187 | 4.5364 | 4.1354 | 4.0528
| 160 | 5.5004 | 4.6104 | 4.1541 | 4.06
| 170 | 5.6938 | 4.689 | 4.1739 | 4.0678
| 180 | 5.8989 | 4.7725 | 4.195 | 4.076
| 190 | 6.1157 | 4.8607 | 4.2172 | 4.0847
| 200 | 6.3443 | 4.9537 | 4.2407 | 4.0938
| 220 | 6.8366 | 5.154 | 4.2913 | 4.1135
| 240 | 7.3758 | 5.3733 | 4.3466 | 4.1351
| 260 | 7.9619 | 5.6117 | 4.4068 | 4.1586
| 280 | 8.5948 | 5.8692 | 4.4718 | 4.1839
| 300 | 9.2747 | 6.1458 | 4.5416 | 4.2111
| 350 | 11.1794 | 6.9206 | 4.7372 | 4.2873
| 400 |  | 7.8147 | 4.9628 | 4.3753
| 450 |  | 8.828 | 5.2186 | 4.475
| 500 |  | 9.9605 | 5.5044 | 4.5864
| 600 |  |  | 6.1664 | 4.8444
| 650 |  |  | 6.5425 | 4.991
| 700 |  |  | 6.9487 | 5.1493
| 800 |  |  | 7.8514 | 5.5012
| 900 |  |  | 8.8744 | 5.8999
| 1000 |  |  | 10.0177 | 6.3456
| 1100 |  |  |  | 6.8381
| 1200 |  |  |  | 7.3776
| 1300 |  |  |  | 7.964
| 1400 |  |  |  | 8.5973
| 1500 |  |  |  | 9.2775
| 1600 |  |  |  | 10.0047
*BPA- Backflow Prevention Assemblies

## Page 8
Pressure Loss Through BPA* (RPZ), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 3 | 4 | 6 | 8
| 50 | 10.1221 | 10.0397 | 10.01
| 52 | 10.1321 | 10.043 | 10.0108
| 54 | 10.1424 | 10.0463 | 10.0117
| 56 | 10.1532 | 10.0498 | 10.0126
| 58 | 10.1643 | 10.0535 | 10.0135
| 60 | 10.1758 | 10.0572 | 10.0144
| 65 | 10.2063 | 10.0672 | 10.0169
| 70 | 10.2393 | 10.0779 | 10.0197
| 75 | 10.2747 | 10.0894 | 10.0226
| 80 | 10.3126 | 10.1017 | 10.0257
| 85 | 10.3529 | 10.1148 | 10.029
| 90 | 10.3956 | 10.1287 | 10.0325
| 95 | 10.4408 | 10.1434 | 10.0362 | 10.0142
| 100 | 10.4884 | 10.1589 | 10.0401 | 10.0157
| 110 | 10.591 | 10.1923 | 10.0485 | 10.019
| 120 | 10.7033 | 10.2289 | 10.0578 | 10.0226
| 130 | 10.8254 | 10.2686 | 10.0678 | 10.0266
| 140 | 10.9573 | 10.3115 | 10.0786 | 10.0308
| 150 | 11.0989 | 10.3576 | 10.0903 | 10.0354
| 160 | 11.2503 | 10.4069 | 10.1027 | 10.0403
| 170 | 11.4115 | 10.4594 | 10.1159 | 10.0455
| 180 | 11.5824 | 10.515 | 10.13 | 10.051
| 190 | 11.7631 | 10.5738 | 10.1448 | 10.0568
| 200 | 11.9536 | 10.6358 | 10.1605 | 10.0629
| 220 | 12.3638 | 10.7693 | 10.1942 | 10.0761
| 240 | 12.8132 | 10.9155 | 10.2311 | 10.0906
| 260 | 13.3016 | 11.0745 | 10.2712 | 10.1063
| 280 | 13.829 | 11.2461 | 10.3145 | 10.1233
| 300 | 14.3956 | 11.4305 | 10.3611 | 10.1416
| 350 |  | 11.9471 | 10.4914 | 10.1927
| 400 |  | 12.5431 | 10.6419 | 10.2517
| 450 |  | 13.2187 | 10.8124 | 10.3185
| 500 |  | 13.9737 | 11.003 | 10.3932
| 600 |  |  | 11.4443 | 10.5662
| 650 |  |  | 11.695 | 10.6646
| 700 |  |  | 11.9658 | 10.7707
| 800 |  |  | 12.5676 | 11.0067
| 900 |  |  | 13.2496 | 11.2741
| 1000 |  |  | 14.0118 | 11.5729
| 1100 |  |  |  | 11.9032
| 1200 |  |  |  | 12.265
| 1300 |  |  |  | 12.6582
| 1400 |  |  |  | 13.0829
| 1500 |  |  |  | 13.539
| 1600 |  |  |  | 14.0267
*BPA- Backflow Prevention Assemblies

## CV (hidden)
Chart Values |  | Flush Tanks |  | Flushometer Valves
WSFU | GPM | WSFU | GPM | WSFU | GPM
1 | 3 | 1 | 3 | 1 | 15
2 | 5 | 2 | 5 | 2 | 15
3 | 6.5 | 3 | 6.5 | 3 | 15
4 | 8 | 4 | 8 | 4 | 15
5 | 9.4 | 5 | 9.4 | 5 | 15
6 | 10.7 | 6 | 10.7 | 6 | 17.4
7 | 11.8 | 7 | 11.8 | 7 | 19.8
8 | 12.8 | 8 | 12.8 | 8 | 22.2
9 | 13.7 | 9 | 13.7 | 9 | 24.6
10 | 14.6 | 10 | 14.6 | 10 | 27
11 | 15.4 | 11 | 15.4 | 11 | 27.8
12 | 16 | 12 | 16 | 12 | 28.6
13 | 16.5 | 13 | 16.5 | 13 | 29.4
14 | 17 | 14 | 17 | 14 | 30.2
15 | 17.5 | 15 | 17.5 | 15 | 31
16 | 18 | 16 | 18 | 16 | 31.8
17 | 18.4 | 17 | 18.4 | 17 | 32.6
18 | 18.8 | 18 | 18.8 | 18 | 33.4
19 | 19.2 | 19 | 19.2 | 19 | 34.2
20 | 19.6 | 20 | 19.6 | 20 | 35
25 | 21.5 | 25 | 21.5 | 25 | 38
30 | 23.3 | 30 | 23.3 | 30 | 42
35 | 24.9 | 35 | 24.9 | 35 | 44
40 | 26.3 | 40 | 26.3 | 40 | 46
45 | 27.7 | 45 | 27.7 | 45 | 48
50 | 29.1 | 50 | 29.1 | 50 | 50
60 | 32 | 60 | 32 | 60 | 54
70 | 35 | 70 | 35 | 70 | 58
80 | 38 | 80 | 38 | 80 | 61.2
90 | 41 | 90 | 41 | 90 | 64.3
100 | 43.5 | 100 | 43.5 | 100 | 67.5
120 | 48 | 120 | 48 | 120 | 73
140 | 52.5 | 140 | 52.5 | 140 | 77
160 | 57 | 160 | 57 | 160 | 81
180 | 61 | 180 | 61 | 180 | 85.5
200 | 65 | 200 | 65 | 200 | 90
225 | 70 | 225 | 70 | 225 | 95.5
250 | 75 | 250 | 75 | 250 | 101
275 | 80 | 275 | 80 | 275 | 104.5
300 | 85 | 300 | 85 | 300 | 108
400 | 105 | 400 | 105 | 400 | 127
500 | 124 | 500 | 124 | 500 | 143
750 | 170 | 750 | 170 | 750 | 177
1000 | 208 | 1000 | 208 | 1000 | 208
1250 | 239 | 1250 | 239 | 1250 | 239
1500 | 269 | 1500 | 269 | 1500 | 269
1750 | 297 | 1750 | 297 | 1750 | 297
2000 | 325 | 2000 | 325 | 2000 | 325
2500 | 380 | 2500 | 380 | 2500 | 380
3000 | 433 | 3000 | 433 | 3000 | 433
4000 | 525 | 4000 | 525 | 4000 | 525
5000 | 593 | 5000 | 593 | 5000 | 593