## Cover Page
Instructions Sheet (MSW2: Small Domestic and/or Large Fire Service Connection*) *2-inch and smaller diameter water service connection is classified as small service connection and 3-inch and larger diameter water service connection is classified as large service connection
DIM*- Domestic Irrigation Mechanical
WSFU*= Water Supply Fixture Units
Page 1:
Step 1: Enter the project address, square #, lot #, DC Water Tracking #, and DCRA Tracking # as applicable at the top of the page. This information will populate top of all other sheets.
Step 2: Select the type of predominant supply systems (flush tanks or flushometer valves).
Step 3: Enter the total number of fixtures for each fixture type as applicable. The total number of fixtures should include all the existing fixtures to remain and all the proposed fixtures to be added as applicable.
Page 2:
Step 4: Select the type of building structure (one- and two-family or other).
Step 5: Enter the total hose bibs and/ or lawn sprinkler, total continuous mechanical, and total intermittent mechanical demands, as applicable. Total DIM* demand is calculated by adding domestic, irrigation, and mechanical demands.
Step 6: Select whether a booster pump is proposed.
Step 7: If a booster pump is proposed, enter the pumped demand. The maximum DIM* demand is calculated based on the Total DIM* and pumped demand.
Step 8: Compute the maximum developed lengths.
Step 9: Compute the minimum available pressures.
Step 10: Use pipe sizing charts on pages 4 & 5 to select the domestic service pipe and distribution pipe sizes based on the WSFU, maximum developed length, and minimum available pressure for the domestic service.
Step 11: Determine the domestic meter size based on AWWA water meter table on this page.
Page 3:
Step 12: If a fire service is proposed, enter the total fire demand.
Step 13: Select whether a fire pump is proposed. If the fire pump is proposed, enter the fire pump flow rating.
Step 14: Enter the pipe length between the supply main and the building, the proposed pipe size, C value, and other pipe losses for fire service connections (as applicable) to calculate total pipe losses between the supply main and the building.
Step 15: Enter the supply main and highest fixture elevations to compute static head loss.
Step 16: Enter the hydrant flow test results.
Step 17: Enter the design pressure at the supply main.
Step 18: Enter the pressure losses due to backflow prevention assembly, and special fixture, as applicable. Enter the pipe losses inside the building. Enter the pressure gain (if any) due to pump.

## Page 1
Project Address: |  |  |  |  | Water Supply Fixture Units Worksheet (MSW2)
Square #:
Lot #:
DC Water Tracking #:
DCRA Tracking #:
Input Cells
Predominant Supply Systems:
|  |  | Fixture Type | Occupancy | Type of Supply Control | Number of Fixtures |  |  | Load Value |  | WSFU
|  |  | Full-bath group** | Private | Flush Tank |  |  | x | 3.6 | =
|  |  |  | Private | Flushometer Valve |  |  | x | 8 | =
|  |  | Half-bath Group** | Private | Flush Tank |  |  | X | 2.6
|  |  | Bathtub (with/ without shower head)** | Private | Faucet |  |  | x | 1.4 | =
|  |  |  | Public | Faucet |  |  | x | 4 | =
|  |  | Bidet | Private | Faucet |  |  | x | 2 | =
|  |  | Combination fixture** | Private | Faucet |  |  | x | 3 | =
|  |  | Dishwashing machine | Private | Automatic |  |  | x | 1.4 | =
|  |  | Drinking Fountain | Office, etc. | 3/8" Valve |  |  | x | 0.25 | =
|  |  | Kitchen sink | Private | Faucet |  |  | x | 1.4 | =
|  |  |  | Commercial | Faucet |  |  | x | 3 | =
|  |  | Laundry tub** | Private | Faucet |  |  | x | 1.4 | =
|  |  | Lavatory sink | Private | Faucet |  |  | x | 0.7 | =
|  |  |  | Public | Faucet |  |  | x | 2 | =
|  |  | Service sink | Public | Faucet |  |  | x | 3 | =
|  |  | Shower head | Private | Mixing Valve |  |  | x | 1.4 | =
|  |  |  | Public | Mixing Valve |  |  | x | 3 | =
|  |  | Urinal** | Public | 1" Flushometer Valve |  |  | x | 10 | =
|  |  |  | Public | 3/4" Flushometer Valve |  |  | x | 5 | =
|  |  |  | Public | Flush Tank |  |  | x | 3 | =
|  |  | Washing machine (8 lb) | Private | Automatic |  |  | x | 1.4 | =
|  |  | Washing machine (8 lb) | Public | Automatic |  |  | X | 3 | =
|  |  | Washing machine (15 lb) | Public | Automatic |  |  | x | 4 | =
|  |  | Water closet | Private | Flush Tank** |  |  | x | 2.2 | =
|  |  |  | Private | Flushometer Valve** |  |  | x | 6 | =
|  |  |  | Private | Flushometer Tank** |  |  | x | 2 | =
|  |  |  | Public | Flushometer Valve |  |  | x | 10 | =
|  |  |  | Public | Flush Tank |  |  | x | 5 | =
|  |  |  | Public | Flushometer Tank |  |  | x | 2 | =
|  |  | Other |  |  |  |  | x | 5 | =
Total WSFU:
[7 empty] | Domestic Demand 1: | [5 empty] | GPM
1 Domestic demand is calculated as per International Plumbing Code 2012 edition.
** See the definition page
Flush Tank
Flushometer Valve

## Page 2
Project Address: |  |  | 0 |  |  |  | Meter Sizing Worksheet (MSW2)
Square #: |  |  | 0
Lot #: |  |  | 0
DC Water Tracking #: |  |  | 0
DCRA Tracking #: |  |  | 0
Input Cells
| Domestic Meter Size | [7 empty] | Maximum Developed Length
| a | Total Water Supply Fixture Units (WSFU) | [5 empty] | wsfu | The maximum developed length= (Actual length of pipe between the source of supply and the most remote fixture) X 1.2.
| b | Domestic Demand | [5 empty] | gpm
| c | Total Hose Bibs and/ or Lawn Sprinkler Demand | [5 empty] | gpm
Dom.
| d | Total Continuous Mechanical Demand | [5 empty] | gpm | a | Distance from water main to curb4 |  |  |  | ft
| e | Total Intermittent Mechanical Demand | [5 empty] | gpm | b | Distance from curb to building face |  |  |  | ft
| f | Total DIM (Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.)) Demand | [5 empty] | gpm | c | Building Length (at the longest point) |  |  |  | ft
[9 empty] | d | Building Width (at the widest point) |  |  |  | ft
[9 empty] | e | Building Height5 |  |  |  | ft
| g | Domestic Booster Pump Proposed? | [6 empty] | f | Length of pipe between source of supply and the most remote fixture (a+b+c+d+e or user entered value)6 |  |  |  | ft
| h | Pumped Demand | [5 empty] | gpm
| i | Maximum DIM Demand (higher of g and h) | [5 empty] | gpm | g | The maximum developed length (value f x 1.2) |  |  |  | ft
| j | Maximum DIM* Demand in WSFU | [5 empty] | wsfu
| k | The Maximum Developed Length | [5 empty] | ft | Minimum Available Pressure
| l | Minimum Available Pressure | [5 empty] | psi | Minimum available pressure = minimum static pressure available from the supply source - static pressure loss due to difference in elevations between the water supply source and the highest water supply outlet - meter loss - backflow prevention device/ assembly loss- any other loss (if any).
| Domestic Service Pipe1 Size | [6 empty] | in
| Domestic Distribution Pipe2 Size | [6 empty] | in
| Domestic/ SAF Meter Size3 | [6 empty] | in
Dom.
[9 empty] | h | Minimum static pressure available from the supply source7 |  |  |  | psi
AWWA Water Meter Standards
| Meter Size |  | High-Normal Flow Rate, gpm |  | Maximum Flow Rate, gpm |  |  |  | i | Static pressure loss (building height/2.31) |  | - | 0 | psi
[9 empty] | j | Additional static pressure loss (if any) |  | - |  | psi
[9 empty] | k | Meter loss8 |  | - |  | psi
| 5/8" EX. ONLY (PD*) |  | 10 |  | 20 |  |  |  | l | Backflow prevention device/ assembly loss8 |  | - |  | psi
| 3/4" EX. ONLY (PD*) |  | 15 |  | 30 |  |  |  | m | Any other loss |  | - |  | psi
| 1" (PD*) |  | 25 |  | 50 |  |  |  | n | Pressure gain due to pump (if any) |  | + |  | psi
| 1-1/2" (PD*) |  | 50 |  | 100 |  |  |  | o | Minimum available pressure (g-h-i-j-k-l+m) |  | = |  | psi
| 2" (PD*) |  | 80 |  | 160 |  |  |  | DIM- Domestic Irrigation Mechanical
| Source: AWWA, M22, 3rd Ed. |  |  | PD*- Positive Displacement
| Designer’s Name: |  |  |  |  | Designer’s Signature: |  |  |  |  | DC License #
1Service Pipe- The pipe from the water main to the water distribution system of the building served. The minimum service pipe size shall be 1" for new construction.
2Distribution Pipe- A pipe within the building structure from the water service pipe to the points of utilization.
3Domestic meter size shall be computed based on the maximum DIM demand excluding fire demand. See AWWA water meter standards on this sheet to determine domestic meter size. SAF meter size will be same as domestic meter size. The System Availability Fee (SAF) will be based on SAF meter size. 4This number can be obtained from DC Water by filling out 'Request For Information Form (Meter Sizing Worksheet)'. The form is available on DC Water's website. This number will be negative if the water main is between the road curb and the property line.
5Distance from ground to ceiling of the highest story.
6This value can be overridden if the actual length of the pipe is based on the design data.
7This number can be obtained from DC Water by filling out 'Request For Information Form (Meter Sizing Worksheet)'. The form is available on DC Water's website.
8See pressure loss values based on AWWA standards on Pages 7, 8, 9, 10 and 11 of this worksheet for a reference.
Yes
No
One- or Two-Family Structure
Other Structure

## Page 3
Project Address: |  | 0 |  |  | Large Fire Service Connection Computations (MSW2)
Square #: |  | 0
Lot #: |  | 0
DC Water Tracking #: |  | 0
DCRA Tracking #: |  | 0
Input Cells
| Fire Demand |  |  |  |  | Hydrant Flow Test Results
| Total Fire Demand (Per NFPA requirements) |  |  |  | gpm | Date of Test:
Static Pressure, psi
| Fire Pump Proposed? |  |  |  |  | Residual Pressure, psi
| Fire Pump Flow Rating |  |  |  | gpm | Available Pressure at the Highest Fixture
| Pump Test Demand (150% of Fire Pump Flow Rating) |  | 0 |  | gpm | a. | Design Pressure at the Main |  |  |  |  | psi
[6 empty] | b. | Total Pipe Losses, psi (See Table A) |  | - |  |  | psi
| Maximum Fire Demand |  | 0 |  | gpm | c. | Static Head Loss (See Table B) |  | - | 0 |  | psi
[6 empty] | d. | Backflow Prevention Assembly Loss |  | - |  |  | psi
| Fire Service Pipe Size, inch |  |  |  | inch | e. | Pipe Losses inside the Building2 |  | - |  |  | psi
[6 empty] | f. | Special Fixture Loss- Other (if any) |  | - |  |  | psi
[6 empty] | g. | Pressure Gain due to the pump |  | + |  |  | psi
| Table A- Total Pipe Losses (Main to the Bldg.) |  |  |  |  | Maximum Pressure Available at the Highest Fixture |  |  | = | 0 |  | psi
| Pipe Length (Supply Main to the Bldg.) |  |  |  | ft
Pipe C Value
| Pipe Friction Losses |  |  |  | psi
| Other Pipe Losses (if any) |  |  |  | psi
| Total Pipe Losses (Main to the Bldg.) |  |  |  | psi
| Velocity1 |  |  |  | fps
Table B- Static Head Loss (Main to Highest Fixture)
| Supply Main Elevation |  |  |  | ft
| Highest Fixture Elevation |  |  |  | ft
| Static Head Loss |  | 0 |  | psi
By signing this document, the designer is responsible for determining required domestic, irrigation, mechanical, and fire flows in addition to the proper sizing of meters. By submitting this application, I affirm that the information provided is correct.
| Designer’s Name: |  |  | Designer’s Signature: |  |  |  | DC License #:
1The maximum recommended flow velocity is 15 fps for ductile iron pipe.
2Values should be provided by the plumbing engineer registered in District of Columbia.

## Conversion Sheet A (hidden)
System Type | FlushTank |  | FlushTank |  | FlushometerValve
|  |  | WSFU | GPM | WSFU | GPM | Domestic Demand WFSU to GPM (FlushTank)
| WSFU | Demand | 1 | 3 | 1 | 15 | Row | #N/A | Row | #N/A
Domestic Demand |  | #N/A | 2 | 5 | 2 | 15 | GPM | #N/A | GPM | #N/A
| #N/A |  | 3 | 6.5 | 3 | 15 | WSFUs | #N/A | WSFUs | #N/A
Fire Demand | #REF! | #REF! | 4 | 8 | 4 | 15
|  |  | 5 | 9.4 | 5 | 15 | Slope | 0
Combined Demand |  |  | 6 | 10.7 | 6 | 17.4 | GPM | #N/A
System Type | FlushTank |  | 7 | 11.8 | 7 | 19.8
| WSFU | Demand | 8 | 12.8 | 8 | 22.2 | Domestic GPM to WSFU (FlushTank) |  |  |  | Fire GPM to WSFU (FlushTank or Flushometer Valve)
| #N/A | 0 | 9 | 13.7 | 9 | 24.6 | Row | #N/A | Row | #N/A | Row | #REF! | Row | #REF!
System Type | Flushometer Valve |  | 10 | 14.6 | 10 | 27 | WSFUs | #N/A | WSFUs | #N/A | WSFUs | #REF! | WSFUs | #REF!
| WSFU | Demand | 11 | 15.4 | 11 | 27.8 | GPM | #N/A | GPM | #N/A | GPM | #REF! | GPM | #REF!
| #N/A | 0 | 12 | 16 | 12 | 28.6
|  |  | 13 | 16.5 | 13 | 29.4 | Slope | 0 |  |  | Slope | 0
System Type | Flushometer Valve |  | 14 | 17 | 14 | 30.2 | WSFU | #N/A |  |  | WSFU | #REF!
| WSFU | Demand | 15 | 17.5 | 15 | 31
Domestic Demand |  | #N/A | 16 | 18 | 16 | 31.8
| #N/A |  | 17 | 18.4 | 17 | 32.6
Fire Demand | #REF! | #REF! | 18 | 18.8 | 18 | 33.4 | Domestic Demand WFSU to GPM (FlushometerValve)
|  |  | 19 | 19.2 | 19 | 34.2 | Row | #N/A | Row | #N/A
|  |  | 20 | 19.6 | 20 | 35 | GPM | #N/A | GPM | #N/A
FlushTank/ Flushometer Valve Value | 1 |  | 25 | 21.5 | 25 | 38 | WSFUs | #N/A | WSFUs | #N/A
|  |  | 30 | 23.3 | 30 | 42
|  |  | 35 | 24.9 | 35 | 44 | Slope | 0
Booster Pump Value | 1 |  | 40 | 26.3 | 40 | 46 | GPM | #N/A
|  |  | 45 | 27.7 | 45 | 48
Fire Pump Value |  |  | 50 | 29.1 | 50 | 50 | Domestic GPM to WSFU (FlushometerValve)
|  |  | 60 | 32 | 60 | 54 | Row | #N/A | Row | #N/A
Type of Occupancy value | 2 |  | 70 | 35 | 70 | 58 | WSFUs | #N/A | WSFUs | #N/A
|  |  | 80 | 38 | 80 | 61.2 | GPM | #N/A | GPM | #N/A
Proposed Meter Type Value | 1 |  | 90 | 41 | 90 | 64.3
|  |  | 100 | 43.5 | 100 | 67.5 | Slope | 0
|  |  | 120 | 48 | 120 | 73 | WSFU | #N/A
Proposed Fire Pump | Input | Output | 140 | 52.5 | 140 | 77
| Yes | 1 | 160 | 57 | 160 | 81
| No |  | 180 | 61 | 180 | 85.5 | Combined GPM to WSFU (FlushTank)
|  |  | 200 | 65 | 200 | 90 | Row | #N/A | Row | #N/A
|  |  | 225 | 70 | 225 | 95.5 | WSFUs | #N/A | WSFUs | #N/A
|  |  | 250 | 75 | 250 | 101 | GPM | #N/A | GPM | #N/A
|  |  | 275 | 80 | 275 | 104.5
|  |  | 300 | 85 | 300 | 108 | Slope | 0
|  |  | 400 | 105 | 400 | 127 | WSFU | #N/A
|  |  | 500 | 124 | 500 | 143
|  |  | 750 | 170 | 750 | 177
|  |  | 1000 | 208 | 1000 | 208 | Combined GPM to WSFU (FlushometerValve)
|  |  | 1250 | 239 | 1250 | 239 | Row | #N/A | Row | #N/A
|  |  | 1500 | 269 | 1500 | 269 | WSFUs | #N/A | WSFUs | #N/A
|  |  | 1750 | 297 | 1750 | 297 | GPM | #N/A | GPM | #N/A
|  |  | 2000 | 325 | 2000 | 325
|  |  | 2500 | 380 | 2500 | 380 | Slope | 0
|  |  | 3000 | 433 | 3000 | 433 | WSFU | #N/A
|  |  | 4000 | 525 | 4000 | 525
|  |  | 5000 | 593 | 5000 | 593

## Conversion Sheet B (hidden)
System Type | FlushTank |  | FlushTank |  | FlushometerValve
|  |  | WSFU | GPM | WSFU | GPM | Domestic Demand WFSU to GPM (FlushTank)
| WSFU | Demand | 1 | 3 | 1 | 15 | Row | #REF! | Row | #REF!
Domestic Demand | #REF! | #REF! | 2 | 5 | 2 | 15 | GPM | #REF! | GPM | #REF!
| #REF! | #REF! | 3 | 6.5 | 3 | 15 | WSFUs | #REF! | WSFUs | #REF!
|  |  | 4 | 8 | 4 | 15
|  |  | 5 | 9.4 | 5 | 15 | Slope | 0
|  |  | 6 | 10.7 | 6 | 17.4 | GPM | #REF!
|  |  | 7 | 11.8 | 7 | 19.8
|  |  | 8 | 12.8 | 8 | 22.2 | Domestic GPM to WSFU (FlushTank)
|  |  | 9 | 13.7 | 9 | 24.6 | Row | #REF! | Row | #REF!
|  |  | 10 | 14.6 | 10 | 27 | WSFUs | #REF! | WSFUs | #REF!
|  |  | 11 | 15.4 | 11 | 27.8 | GPM | #REF! | GPM | #REF!
|  |  | 12 | 16 | 12 | 28.6
|  |  | 13 | 16.5 | 13 | 29.4 | Slope | 0
System Type | Flushometer Valve |  | 14 | 17 | 14 | 30.2 | WSFU | #REF!
| WSFU | Demand | 15 | 17.5 | 15 | 31
Domestic Demand | #REF! | #REF! | 16 | 18 | 16 | 31.8
| #REF! | #REF! | 17 | 18.4 | 17 | 32.6
|  |  | 18 | 18.8 | 18 | 33.4 | Domestic Demand WFSU to GPM (FlushometerValve)
|  |  | 19 | 19.2 | 19 | 34.2 | Row | #REF! | Row | #REF!
|  |  | 20 | 19.6 | 20 | 35 | GPM | #REF! | GPM | #REF!
|  |  | 25 | 21.5 | 25 | 38 | WSFUs | #REF! | WSFUs | #REF!
|  |  | 30 | 23.3 | 30 | 42
|  |  | 35 | 24.9 | 35 | 44 | Slope | 0
|  |  | 40 | 26.3 | 40 | 46 | GPM | #REF!
|  |  | 45 | 27.7 | 45 | 48
|  |  | 50 | 29.1 | 50 | 50 | Domestic GPM to WSFU (FlushometerValve)
|  |  | 60 | 32 | 60 | 54 | Row | #REF! | Row | #REF!
|  |  | 70 | 35 | 70 | 58 | WSFUs | #REF! | WSFUs | #REF!
|  |  | 80 | 38 | 80 | 61.2 | GPM | #REF! | GPM | #REF!
|  |  | 90 | 41 | 90 | 64.3
|  |  | 100 | 43.5 | 100 | 67.5 | Slope | 0
|  |  | 120 | 48 | 120 | 73 | WSFU | #REF!
|  |  | 140 | 52.5 | 140 | 77
|  |  | 160 | 57 | 160 | 81
|  |  | 180 | 61 | 180 | 85.5
|  |  | 200 | 65 | 200 | 90
|  |  | 225 | 70 | 225 | 95.5
|  |  | 250 | 75 | 250 | 101
|  |  | 275 | 80 | 275 | 104.5
|  |  | 300 | 85 | 300 | 108
|  |  | 400 | 105 | 400 | 127
|  |  | 500 | 124 | 500 | 143
|  |  | 750 | 170 | 750 | 177
|  |  | 1000 | 208 | 1000 | 208
|  |  | 1250 | 239 | 1250 | 239
|  |  | 1500 | 269 | 1500 | 269
|  |  | 1750 | 297 | 1750 | 297
|  |  | 2000 | 325 | 2000 | 325
|  |  | 2500 | 380 | 2500 | 380
|  |  | 3000 | 433 | 3000 | 433
|  |  | 4000 | 525 | 4000 | 525
|  |  | 5000 | 593 | 5000 | 593

## Page 4
PIPE SIZING CHART (PRESSURE RANGE 30-39 PSI AND 40-49 PSI
PIPE SIZING CHART FOR PRESSURE RANGE 30-39 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 2.5 | 2 | 1.5 | 1.5 | 1 | 1 | 0.5 | 0.5 | 0 | 0 | 0.75 | 0.5
| 9.5 | 7.5 | 6 | 5.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.5 | 0.75 | 0.75
| 32 | 25 | 20 | 16.5 | 11 | 9 | 7.8 | 6.5 | 5.5 | 4.5 | 0.75 | 1
| 32 | 32 | 27 | 21 | 13.5 | 10 | 8 | 7 | 5.5 | 5 | 1 | 1
| 32 | 32 | 32 | 32 | 30 | 24 | 20 | 17 | 13 | 10.5 | 0.75 | 1.25
| 80 | 80 | 70 | 61 | 45 | 34 | 27 | 22 | 16 | 12 | 1 | 1.25
| 80 | 80 | 80 | 75 | 54 | 40 | 31 | 25 | 17.5 | 13 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 84 | 73 | 64 | 56 | 45 | 36 | 1 | 1.5
| 151 | 151 | 151 | 151 | 117 | 92 | 79 | 69 | 54 | 43 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 128 | 99 | 83 | 72 | 56 | 45 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 1 | 2
| 275 | 275 | 275 | 275 | 258 | 223 | 196 | 174 | 144 | 122 | 1.5 | 2
| 365 | 365 | 365 | 365 | 318 | 266 | 229 | 201 | 160 | 134 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 495 | 448 | 409 | 353 | 311 | 2 | 2.5
PIPE SIZING CHART FOR PRESSURE RANGE 40-49 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 3 | 2.5 | 2 | 1.5 | 1.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.75 | 0.5
| 9.5 | 9.5 | 8.5 | 7 | 5.5 | 4.5 | 3.5 | 3 | 2.5 | 2 | 0.75 | 0.75
| 32 | 32 | 32 | 26 | 18 | 13.5 | 10.5 | 9 | 7.5 | 6 | 0.75 | 1
| 32 | 32 | 32 | 32 | 21 | 15 | 11.5 | 9.5 | 7.5 | 6.5 | 1 | 1
| 32 | 32 | 32 | 32 | 32 | 32 | 32 | 27 | 21 | 16.5 | 0.75 | 1.25
| 80 | 80 | 80 | 80 | 65 | 52 | 42 | 35 | 26 | 20 | 1 | 1.25
| 80 | 80 | 80 | 80 | 75 | 59 | 48 | 39 | 28 | 21 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 78 | 65 | 55 | 1 | 1.5
| 151 | 151 | 151 | 151 | 151 | 130 | 109 | 93 | 75 | 63 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 151 | 139 | 115 | 98 | 77 | 64 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1 | 2
| 275 | 275 | 275 | 275 | 275 | 275 | 264 | 238 | 198 | 169 | 1.5 | 2
| 365 | 365 | 365 | 365 | 365 | 349 | 304 | 270 | 220 | 185 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 533 | 533 | 528 | 456 | 403 | 2 | 2.5
Source: International Plumbing Code 2012 edition

## Page 5
PIPE SIZING CHART (PRESSURE RANGE 50-59 PSI AND 60+ PSI)
PIPE SIZING CHART FOR PRESSURE RANGE 50-59 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 3 | 3 | 2.5 | 2 | 1.5 | 1 | 1 | 1 | 0.5 | 0.5 | 0.75 | 0.5
| 9.5 | 9.5 | 9.5 | 8.5 | 6.5 | 5 | 4.5 | 4 | 3 | 2.5 | 0.75 | 0.75
| 32 | 32 | 32 | 32 | 25 | 18.5 | 14.5 | 12 | 9.5 | 8 | 0.75 | 1
| 32 | 32 | 32 | 32 | 30 | 22 | 16.5 | 13 | 10 | 8 | 1 | 1
| 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 29 | 24 | 0.75 | 1.25
| 80 | 80 | 80 | 80 | 80 | 68 | 57 | 48 | 35 | 28 | 1 | 1.25
| 80 | 80 | 80 | 80 | 80 | 75 | 63 | 53 | 39 | 29 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 82 | 70 | 1 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 139 | 120 | 94 | 79 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 146 | 126 | 97 | 81 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1 | 2
| 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 247 | 213 | 1.5 | 2
| 365 | 365 | 365 | 365 | 365 | 365 | 365 | 329 | 272 | 232 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 486 | 2 | 2.5
PIPE SIZING CHART FOR PRESSURE RANGE OVER 60 PSI
DEVELOPED LENGTH (FT)
| 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | METER AND SERVICE PIPE SIZE | DISTRIBUTION PIPE SIZE
Water Supply Fixture Units | 3 | 3 | 3 | 2.5 | 2 | 1.5 | 1.5 | 1 | 1 | 0.5 | 0.75 | 0.5
| 9.5 | 9.5 | 9.5 | 9.5 | 7.5 | 6 | 5 | 4.5 | 3.5 | 3 | 0.75 | 0.75
| 32 | 32 | 32 | 32 | 32 | 24 | 19.5 | 15.5 | 11.5 | 9.5 | 0.75 | 1
| 32 | 32 | 32 | 32 | 32 | 28 | 28 | 17 | 12 | 9.5 | 1 | 1
| 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 0.75 | 1.25
| 80 | 80 | 80 | 80 | 80 | 80 | 69 | 60 | 46 | 36 | 1 | 1.25
| 80 | 80 | 80 | 80 | 80 | 80 | 76 | 65 | 50 | 38 | 1.5 | 1.25
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 84 | 1 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 151 | 144 | 114 | 94 | 1.5 | 1.5
| 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 118 | 97 | 2 | 1.5
| 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1 | 2
| 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 252 | 1.5 | 2
| 365 | 368 | 368 | 368 | 368 | 368 | 368 | 368 | 318 | 273 | 2 | 2
| 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 533 | 2 | 2.5
Source: International Plumbing Code 2012 edition

## Page 6
DEFINITIONS (MSW2)
Full-bath Group (Flush Tank) - 1 Tank Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Full-bath Group (Flushometer Valve)- 1 Flushometer Toilet, 1 Bathroom Sink and either 1 shower, 1 tub or 1 shower/tub combination.
Half-bath Group (Flush Tank)- 1 Tank Toilet and 1 Bathroom Sink
Bathtub / Shower Combination- This fixture has a bathtub as the basin base with a bath shower atop it and is located in PRIVATE space. This fixture can only use either the tub faucet OR the shower head. Not both at the same time.
Combination Fixture- This fixture combines the functions of a sink and a toilet into a single fixture and is located in PRIVATE space.
Water Closet (Tank Toilet)- This is a toilet that has a tank on the back that holds water. If there is no tank the fixture is called a Flushometer Valve toilet.
Water Closet (Flushometer Valve)- This type of toilet has no tank to store the water on the back. The water pipe comes directly out of the wall and fills the bowl.
Water Closet (Flushometer Tank)- This fixture combines a Flushometer Valve with a tank. The valve allows a certain amount of water to fill the tank quickly at a high rate.
Laundry Tub- A sink located in a laundry room or utility room.
Hose Bibs (ALL Public and Private Bibs)- An outside faucet.
Urinal (1" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 1" valve.
Urinal (3/4" Flushometer Valve)- A bathroom urinal located in PUBLIC space with a 3/4" valve.
Urinal (Flush Tank)- A bathroom urinal located in PUBLIC space with a tank.
Domestic Demand- The water used by the fixtures and the mechanical equipment excluding fire and irrigation only.
IPC- International Plumbing Code

## Page 7
Pressure Loss Through Water Meters, PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Meter Size, in.
|  | 0.625 | 0.75 | 1 | 1.5 | 2
| 1 | 0.04 | 0.01679 | 0.0060131
| 2 | 0.15111 | 0.067159 | 0.024053
| 3 | 0.34 | 0.15111 | 0.054118
| 4 | 0.60445 | 0.26863 | 0.09621
| 5 | 0.94445 | 0.41974 | 0.15033
| 6 | 1.36 | 0.60443 | 0.21647
| 7 | 1.8511 | 0.82269 | 0.29464
| 8 | 2.4178 | 1.0745 | 0.38484 | 0.095737
| 9 | 3.06 | 1.36 | 0.48706 | 0.12117
| 10 | 3.7778 | 1.679 | 0.60131 | 0.14959
| 11 | 4.5711 | 2.0315 | 0.72759 | 0.181
| 12 | 5.44 | 2.4177 | 0.86589 | 0.21541
| 13 | 6.3845 | 2.8375 | 1.0162 | 0.25281 | 0.099091
| 14 | 7.4045 | 3.2908 | 1.1786 | 0.29319 | 0.11492
| 15 | 8.5001 | 3.7777 | 1.353 | 0.33657 | 0.13193
| 16 | 9.6712 | 4.2982 | 1.5394 | 0.38295 | 0.1501
| 17 | 10.9179 | 4.8522 | 1.7378 | 0.43231 | 0.16945
| 18 | 12.2401 | 5.4399 | 1.9483 | 0.48467 | 0.18997
| 19 | 13.6379 | 6.0611 | 2.1707 | 0.54002 | 0.21167
| 20 | 15.1112 | 6.7159 | 2.4053 | 0.59836 | 0.23453
| 22 |  | 8.1262 | 2.9104 | 0.72401 | 0.28379
| 24 |  | 9.6708 | 3.4636 | 0.86163 | 0.33773
| 26 |  | 11.3498 | 4.0649 | 1.0112 | 0.39636
| 28 |  | 13.1631 | 4.7143 | 1.1728 | 0.45969
| 30 |  | 15.1107 | 5.4118 | 1.3463 | 0.5277
| 32 |  |  | 6.1574 | 1.5318 | 0.60041
| 34 |  |  | 6.9512 | 1.7292 | 0.67781
| 36 |  |  | 7.793 | 1.9387 | 0.75989
| 38 |  |  | 8.683 | 2.1601 | 0.84667
| 40 |  |  | 9.621 | 2.3934 | 0.93814
| 42 |  |  | 10.6072 | 2.6387 | 1.0343
| 44 |  |  | 11.6414 | 2.896 | 1.1351
| 46 |  |  | 12.7238 | 3.1653 | 1.2407
| 48 |  |  | 13.8543 | 3.4465 | 1.3509
| 50 |  |  | 15.0328 | 3.7397 | 1.4658
| 52 |  |  |  | 4.0449 | 1.5855
| 54 |  |  |  | 4.362 | 1.7098
| 56 |  |  |  | 4.6911 | 1.8388
| 58 |  |  |  | 5.0322 | 1.9724
| 60 |  |  |  | 5.3852 | 2.1108
| 65 |  |  |  | 6.3201 | 2.4773
| 70 |  |  |  | 7.3299 | 2.8731
| 75 |  |  |  | 8.4144 | 3.2981
| 80 |  |  |  | 9.5737 | 3.7526
| 85 |  |  |  | 10.8078 | 4.2363
| 90 |  |  |  | 12.1167 | 4.7493
| 95 |  |  |  | 13.5004 | 5.2917
| 100 |  |  |  | 14.9589 | 5.8634
| 110 |  |  |  |  | 7.0947
| 120 |  |  |  |  | 8.4433
| 130 |  |  |  |  | 9.9091
| 140 |  |  |  |  | 11.4922
| 150 |  |  |  |  | 13.1926
| 160 |  |  |  |  | 15.0102

## Page 8
Pressure Loss Through BPA* (DCV), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 0.75 | 1 | 1.5 | 2
| 1 | 4.0068 | 4.0024 | 4.0006 | 4.0002
| 2 | 4.0271 | 4.0095 | 4.0024 | 4.0009
| 3 | 4.0611 | 4.0214 | 4.0054 | 4.0021
| 4 | 4.1086 | 4.038 | 4.0096 | 4.0037
| 5 | 4.1697 | 4.0593 | 4.0151 | 4.0058
| 6 | 4.2443 | 4.0854 | 4.0217 | 4.0084
| 7 | 4.3326 | 4.1163 | 4.0295 | 4.0114
| 8 | 4.4344 | 4.1519 | 4.0386 | 4.0149
| 9 | 4.5498 | 4.1923 | 4.0488 | 4.0189
| 10 | 4.6787 | 4.2374 | 4.0603 | 4.0233
| 11 | 4.8213 | 4.2872 | 4.0729 | 4.0282
| 12 | 4.9774 | 4.3418 | 4.0868 | 4.0336
| 13 | 5.1471 | 4.4011 | 4.1019 | 4.0394
| 14 | 5.3303 | 4.4652 | 4.1182 | 4.0457
| 15 | 5.5271 | 4.5341 | 4.1356 | 4.0525
| 16 | 5.7376 | 4.6076 | 4.1543 | 4.0597
| 17 | 5.9615 | 4.686 | 4.1742 | 4.0674
| 18 | 6.1991 | 4.769 | 4.1953 | 4.0755
| 19 | 6.4502 | 4.8569 | 4.2176 | 4.0842
| 20 | 6.7149 | 4.9494 | 4.2411 | 4.0932
| 22 | 7.2851 | 5.1488 | 4.2918 | 4.1128
| 24 | 7.9095 | 5.3672 | 4.3472 | 4.1343
| 26 | 8.5882 | 5.6046 | 4.4075 | 4.1576
| 28 | 9.3213 | 5.8609 | 4.4726 | 4.1828
| 30 | 10.1086 | 6.1362 | 4.5425 | 4.2098
| 32 |  | 6.4306 | 4.6173 | 4.2387
| 34 |  | 6.7439 | 4.6969 | 4.2695
| 36 |  | 7.0762 | 4.7813 | 4.3021
| 38 |  | 7.4275 | 4.8705 | 4.3366
| 40 |  | 7.7978 | 4.9645 | 4.373
| 42 |  | 8.187 | 5.0634 | 4.4112
| 44 |  | 8.5953 | 5.1671 | 4.4513
| 46 |  | 9.0225 | 5.2756 | 4.4933
| 48 |  | 9.4688 | 5.3889 | 4.5371
| 50 |  | 9.934 | 5.5071 | 4.5828
| 52 |  |  | 5.63 | 4.6304
| 54 |  |  | 5.7578 | 4.6798
| 56 |  |  | 5.8904 | 4.7311
| 58 |  |  | 6.0279 | 4.7842
| 60 |  |  | 6.1702 | 4.8392
| 65 |  |  | 6.5469 | 4.9849
| 70 |  |  | 6.9538 | 5.1423
| 75 |  |  | 7.3909 | 5.3113
| 80 |  |  | 7.8581 | 5.492
| 85 |  |  | 8.3554 | 5.6843
| 90 |  |  | 8.8828 | 5.8883
| 95 |  |  | 9.4405 | 6.1039
| 100 |  |  | 10.0282 | 6.3312
| 110 |  |  |  | 6.8208
| 120 |  |  |  | 7.357
| 130 |  |  |  | 7.9398
| 140 |  |  |  | 8.5692
| 150 |  |  |  | 9.2452
| 160 |  |  |  | 9.9679
*BPA- Backflow Prevention Assemblies

## Page 9
Pressure Loss Through BPA* (DCV), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 3 | 4 | 6 | 8
50
52
| 54 | 4.1709
| 56 | 4.1838 | 4.0748
| 58 | 4.1972 | 4.0802
| 60 | 4.211 | 4.0858
| 65 | 4.2476 | 4.1007
| 70 | 4.2872 | 4.1168 | 4.0295
| 75 | 4.3297 | 4.1341 | 4.0338
| 80 | 4.3751 | 4.1526 | 4.0385
| 85 | 4.4234 | 4.1723 | 4.0435
| 90 | 4.4747 | 4.1931 | 4.0487
| 95 | 4.5289 | 4.2152 | 4.0543 | 4.0212
| 100 | 4.5861 | 4.2384 | 4.0602 | 4.0235
| 110 | 4.7092 | 4.2885 | 4.0728 | 4.0284
| 120 | 4.8439 | 4.3433 | 4.0867 | 4.0338
| 130 | 4.9905 | 4.4029 | 4.1017 | 4.0396
| 140 | 5.1487 | 4.4673 | 4.1179 | 4.046
| 150 | 5.3187 | 4.5364 | 4.1354 | 4.0528
| 160 | 5.5004 | 4.6104 | 4.1541 | 4.06
| 170 | 5.6938 | 4.689 | 4.1739 | 4.0678
| 180 | 5.8989 | 4.7725 | 4.195 | 4.076
| 190 | 6.1157 | 4.8607 | 4.2172 | 4.0847
| 200 | 6.3443 | 4.9537 | 4.2407 | 4.0938
| 220 | 6.8366 | 5.154 | 4.2913 | 4.1135
| 240 | 7.3758 | 5.3733 | 4.3466 | 4.1351
| 260 | 7.9619 | 5.6117 | 4.4068 | 4.1586
| 280 | 8.5948 | 5.8692 | 4.4718 | 4.1839
| 300 | 9.2747 | 6.1458 | 4.5416 | 4.2111
| 350 | 11.1794 | 6.9206 | 4.7372 | 4.2873
| 400 |  | 7.8147 | 4.9628 | 4.3753
| 450 |  | 8.828 | 5.2186 | 4.475
| 500 |  | 9.9605 | 5.5044 | 4.5864
| 600 |  |  | 6.1664 | 4.8444
| 650 |  |  | 6.5425 | 4.991
| 700 |  |  | 6.9487 | 5.1493
| 800 |  |  | 7.8514 | 5.5012
| 900 |  |  | 8.8744 | 5.8999
| 1000 |  |  | 10.0177 | 6.3456
| 1100 |  |  |  | 6.8381
| 1200 |  |  |  | 7.3776
| 1300 |  |  |  | 7.964
| 1400 |  |  |  | 8.5973
| 1500 |  |  |  | 9.2775
| 1600 |  |  |  | 10.0047
*BPA- Backflow Prevention Assemblies

## Page 10
Pressure Loss Through BPA* (RPZ), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 0.75 | 1 | 1.5 | 2
| 1 | 10.0111 | 10.0032 | 10.0006 | 10.0002
| 2 | 10.0443 | 10.0127 | 10.0024 | 10.0009
| 3 | 10.0997 | 10.0285 | 10.0054 | 10.0021
| 4 | 10.1772 | 10.0506 | 10.0096 | 10.0037
| 5 | 10.2769 | 10.0791 | 10.0151 | 10.0058
| 6 | 10.3987 | 10.1139 | 10.0217 | 10.0084
| 7 | 10.5426 | 10.1551 | 10.0295 | 10.0114
| 8 | 10.7087 | 10.2025 | 10.0386 | 10.0149
| 9 | 10.897 | 10.2563 | 10.0488 | 10.0189
| 10 | 11.1074 | 10.3165 | 10.0603 | 10.0233
| 11 | 11.34 | 10.3829 | 10.0729 | 10.0282
| 12 | 11.5947 | 10.4557 | 10.0868 | 10.0336
| 13 | 11.8715 | 10.5349 | 10.1019 | 10.0394
| 14 | 12.1705 | 10.6203 | 10.1182 | 10.0457
| 15 | 12.4917 | 10.7121 | 10.1356 | 10.0525
| 16 | 12.835 | 10.8102 | 10.1543 | 10.0597
| 17 | 13.2004 | 10.9146 | 10.1742 | 10.0674
| 18 | 13.588 | 11.0254 | 10.1953 | 10.0755
| 19 | 13.9977 | 11.1425 | 10.2176 | 10.0842
| 20 | 14.4296 | 11.2659 | 10.2411 | 10.0932
| 22 | 15.3598 | 11.5318 | 10.2918 | 10.1128
| 24 | 16.3786 | 11.8229 | 10.3472 | 10.1343
| 26 | 17.486 | 12.1394 | 10.4075 | 10.1576
| 28 | 18.682 | 12.4812 | 10.4726 | 10.1828
| 30 | 19.9666 | 12.8483 | 10.5425 | 10.2098
| 32 |  | 13.2408 | 10.6173 | 10.2387
| 34 |  | 13.6585 | 10.6969 | 10.2695
| 36 |  | 14.1016 | 10.7813 | 10.3021
| 38 |  | 14.57 | 10.8705 | 10.3366
| 40 |  | 15.0637 | 10.9645 | 10.373
| 42 |  | 15.5827 | 11.0634 | 10.4112
| 44 |  | 16.1271 | 11.1671 | 10.4513
| 46 |  | 16.6967 | 11.2756 | 10.4933
| 48 |  | 17.2917 | 11.3889 | 10.5371
| 50 |  | 17.912 | 11.5071 | 10.5828
| 52 |  |  | 11.63 | 10.6304
| 54 |  |  | 11.7578 | 10.6798
| 56 |  |  | 11.8904 | 10.7311
| 58 |  |  | 12.0279 | 10.7842
| 60 |  |  | 12.1702 | 10.8392
| 65 |  |  | 12.5469 | 10.9849
| 70 |  |  | 12.9538 | 11.1423
| 75 |  |  | 13.3909 | 11.3113
| 80 |  |  | 13.8581 | 11.492
| 85 |  |  | 14.3554 | 11.6843
| 90 |  |  | 14.8828 | 11.8883
| 95 |  |  | 15.4405 | 12.1039
| 100 |  |  | 16.0282 | 12.3312
| 110 |  |  |  | 12.8208
| 120 |  |  |  | 13.357
| 130 |  |  |  | 13.9398
| 140 |  |  |  | 14.5692
| 150 |  |  |  | 15.2452
| 160 |  |  |  | 15.9679
*BPA- Backflow Prevention Assemblies

## Page 11
Pressure Loss Through BPA* (RPZ), PSI For Reference Only (Source: AWWA, M22, 3rd Ed.)
| Flow, GPM | Nominal Size, in.
|  | 3 | 4 | 6 | 8
| 50 | 10.1221 | 10.0397 | 10.01
| 52 | 10.1321 | 10.043 | 10.0108
| 54 | 10.1424 | 10.0463 | 10.0117
| 56 | 10.1532 | 10.0498 | 10.0126
| 58 | 10.1643 | 10.0535 | 10.0135
| 60 | 10.1758 | 10.0572 | 10.0144
| 65 | 10.2063 | 10.0672 | 10.0169
| 70 | 10.2393 | 10.0779 | 10.0197
| 75 | 10.2747 | 10.0894 | 10.0226
| 80 | 10.3126 | 10.1017 | 10.0257
| 85 | 10.3529 | 10.1148 | 10.029
| 90 | 10.3956 | 10.1287 | 10.0325
| 95 | 10.4408 | 10.1434 | 10.0362 | 10.0142
| 100 | 10.4884 | 10.1589 | 10.0401 | 10.0157
| 110 | 10.591 | 10.1923 | 10.0485 | 10.019
| 120 | 10.7033 | 10.2289 | 10.0578 | 10.0226
| 130 | 10.8254 | 10.2686 | 10.0678 | 10.0266
| 140 | 10.9573 | 10.3115 | 10.0786 | 10.0308
| 150 | 11.0989 | 10.3576 | 10.0903 | 10.0354
| 160 | 11.2503 | 10.4069 | 10.1027 | 10.0403
| 170 | 11.4115 | 10.4594 | 10.1159 | 10.0455
| 180 | 11.5824 | 10.515 | 10.13 | 10.051
| 190 | 11.7631 | 10.5738 | 10.1448 | 10.0568
| 200 | 11.9536 | 10.6358 | 10.1605 | 10.0629
| 220 | 12.3638 | 10.7693 | 10.1942 | 10.0761
| 240 | 12.8132 | 10.9155 | 10.2311 | 10.0906
| 260 | 13.3016 | 11.0745 | 10.2712 | 10.1063
| 280 | 13.829 | 11.2461 | 10.3145 | 10.1233
| 300 | 14.3956 | 11.4305 | 10.3611 | 10.1416
| 350 |  | 11.9471 | 10.4914 | 10.1927
| 400 |  | 12.5431 | 10.6419 | 10.2517
| 450 |  | 13.2187 | 10.8124 | 10.3185
| 500 |  | 13.9737 | 11.003 | 10.3932
| 600 |  |  | 11.4443 | 10.5662
| 650 |  |  | 11.695 | 10.6646
| 700 |  |  | 11.9658 | 10.7707
| 800 |  |  | 12.5676 | 11.0067
| 900 |  |  | 13.2496 | 11.2741
| 1000 |  |  | 14.0118 | 11.5729
| 1100 |  |  |  | 11.9032
| 1200 |  |  |  | 12.265
| 1300 |  |  |  | 12.6582
| 1400 |  |  |  | 13.0829
| 1500 |  |  |  | 13.539
| 1600 |  |  |  | 14.0267
*BPA- Backflow Prevention Assemblies